## Register list
Address space version
Object | Parameter | R/W | Modbus Table | Modbus Address | Data type | Description | TR403 - BigTable | 1.0 FWPKG 4 | 2.0 FWPKG 6 | 3.0 FWPKG 8 | 3.1 FWPKG 10 | 3.2 FWPKG 12 | 3.3 FWPKG 14 | 3.4 FWPKG 16 | Comments
GENERAL BLOCKING SOURCES
| 0 NONE 1 UNKNOWN 2 CONTACT 3 FLOOR_TEMP 4 LOW_ENERGY 5 AIR_TEMP 6 DEW_POINT 7 OUTDOOR_TEMP 8 FAULT (general fault, e.g. missing sensors) 9 FAULT_HTCO 10 PERIODIC_ACTIVATION 11 BMS 12 DEADBAND 13 DRYING 14 HEATING/COOLING MODE 15 INSUFFICIENT DEMAND 16 COOLDOWN PERIOD 17 HCW SOURCE NOT RELEASED 18 ROOM MODE 19 SYSTEM IS INITIALIZING 20 SYSTEM IS SHUTTING DOWN 21 NO OUTPUT 22 FIRST OPEN ACTIVATION 23 ROOM WITH NO TEMP SOURCE 24 HCWS ELEMENTS BLOCKED The number of blocking sources is still growing. There can be another values than listed in this documentation. |  |  |  |  | Purpose of the modbus interface (Use cases) * it is NOT a user interface * it is NOT an installer interface * It shall alow following: 1. See all warnings and errors 2. Optimize the system by expert (tuning) a. Power consumption b. Reliability c. Suppress activity of system parts (e.g. circulation) 3. Restrict user posibilities & reset user settings a. Set UI access levels b. Reset temperature correction made by user (hotel) c. Basic setup - manual control
PERIPHERAL TYPE
0x0 - DHW-201 0x1 - not used 0x2 - not used 0x3 - not used 0x4 - LCD-200 0x5 - RT-201 0x6 - RT-250 0x7 - RS-211 0x8 - RS-251 0x9 - RT-250IR 0xA - EU-208-A 0xB - EU-206-VFR 0xC - ET-250 0xD - ET-210 0xE - VH-250 0xF - not used 0x11E0 - CCU-208
LOCATION
Location |  |  |  | 000xx |  | This object contains values shared across all objects in the location.
| Aggregated warning | R | Discrete Inputs | 1 |  | A problem is pending in whole system (Location) | - | YES | YES | YES | YES | YES | YES | YES
| Aggregated error | R | Discrete Inputs | 2 |  | A critical problem is pending in whole system (Location) | - | YES | YES | YES | YES | YES | YES | YES
-
| Address space major version | R | Input Register | 1 | val_u1 | = 3 (Incremented on incompatible change) | - | YES | CHANGED | CHANGED | YES | YES | YES | YES
| Address space minor version | R | Input Register | 2 | val_u1 | = 1 (Incremented on compatible change) | - | YES | YES | YES | CHANGED | CHANGED | CHANGED | YES
| - | R | Input Register | 00003-00009 | - | reserved for modbus related things | - | YES | YES | YES | YES | YES | YES | YES
| Dev type | R | Input Register | 10 | val_u1 | 1 - CCU-208 2 - DHW-201 (Calefa) | - | YES | YES | YES | YES | YES | YES | YES
| Dev hw version | R | Input Register | 11 | val_u1 |  | device.hw_version | YES | YES | YES | YES | YES | YES | YES
| Dev sw version | R | Input Register | 12 | val_u1 |  | device.sw_version | YES | YES | YES | YES | YES | YES | YES
| Dev sw version minor | R | Input Register | 13 | val_u1 |  | device.sw_version_minor | YES | YES | YES | YES | YES | YES | YES
| Dev serial number prefix | R | Input Register | 14 | val_u2 | = 1530 | device.serial_prefix | YES | YES | YES | YES | YES | YES | YES
| Dev serial number | R | Input Register | 00015-00016 | val_u4 |  | device.serial | YES | YES | YES | YES | YES | YES | YES
| - | R | Input Register | 00017-00019 | - | reserved for additional device descriptors | - | YES | YES | YES | YES | YES | YES | YES
| Heating/Cooling mode | R | Input Register | 20 | val_u1 | 0 - HEATING 1 - COOLING | location.hc_mode | - | - | - | YES | YES | YES | YES
YES
| Address space major version | R/W | Holding register | 1 | val_u1 | = 3 (Incremented on incompatible change) | - | YES | CHANGED | CHANGED | YES | YES | YES | YES
| Address space minor version | R/W | Holding register | 2 | val_u1 | = 1 (Incremented on compatible change) | - | YES | YES | YES | CHANGED | YES | YES | YES
| Modbus slave address | R/W | Holding register | 3 | val_u1 | Allowed values: 1 to 247 Default: 1 | location.modbus_addr | YES | YES | YES | YES | YES | YES | YES
| Modbus baudrate | R/W | Holding register | 4 | val_u2 | Allowed values: 9600, 19200, 38400, 57600 Default:19200 | location.modbus_baudrate | YES | YES | YES | YES | YES | YES | YES
| Modbus mode | R/W | Holding register | 5 | val_u1 | 0 DISABLED 1 READ_ONLY 2 READ_WRITE 3 WRITE_WITH_PASSWORD Default: 0 | location.modbus_mode | YES | YES | EXTENDED | YES | YES | YES | YES
| Modbus password | W | Holding register | 6 | val_u2 | When Modbus mode = WRITE_WITH_PASSWORD, the write commands are disabled until this register is written by a valid password. Once the password is written, the the write comands are accepted for next 11 minutes. Then the password has to be set again. Two steps are required for password change: 1. Write the old password 2. Write the new password before 11 minutes elapses. Default password: 1234, Write only, range for password is 1 - 65534 |  | - | - | YES | YES | YES | YES | YES
| Modbus parity | R/W | Holding register | 7 | val_u1 | 0 - NONE 1 - ODD 2 - EVEN | location.modbus_parity | - | - | - | YES | YES | YES | YES
| Modbus stop bits | R/W | Holding register | 8 | val_u1 | 0 - 1 STOP BIT 1 - 2 STOP BITS | location.modbus_stop_bits | - | - | - | YES | YES | YES | YES
| - | R/W | Holding register | 9 | - | Reserved for modbus related things | - | - | - | - | - | - | - | -
| Location name | R/W | Holding register | 00010-00025 | val_utf8 | Placeholder for 32 bytes of location description. See “working with strings” chapter for more info. | location.name | YES | YES | YES | YES | YES | YES | YES
| Standby | R/W | Holding register | 26 | val_u1 | 0 OFF 1 ON | location.standby | YES | YES | YES | YES | YES | YES | YES
| Vacation | R/W | Holding register | 27 | val_u1 | 0 OFF 1 ON | location.vacation | YES | YES | YES | YES | YES | YES | YES
| Datetime | R/W | Holding register | 00028-00029 | val_u4 | Current time - unit timestamp format - localtime including DST (if enabled) - minimum date is 2018-01-01 00:00:00 - maximum date is 2099-12-30 23:59:59 | - | - | - | YES | YES | YES | YES | YES
| Daylight saving time allowed | R/W | Holding register | 30 | val_u1 | 0 Disabled 1 Enabled | location.dst_enabled | - | - | YES | YES | YES | YES | YES
| Cooling minimum outdoor temperature | R/W | Holding register | 31 | val_d2_fp100 | Only available in hardware profiles, which support cooling. Cooling is blocked, when outdoor temperature is lower than this value. In profiles which support cooling, minimum outdoor temp for cooling must be >= maximum outdoor temp for heating | location.hc_cooling_min_outdoor_temp | - | - | YES | YES | YES | YES | YES
| Heating maximum outdoor temperature | R/W | Holding register | 32 | val_d2_fp100 | Heating is blocked, when outdoor temperature is higher than this value. In profiles which support cooling, maximum outdoor temp for heating must be <= minimum outdoor temp for cooling | location.hc_heating_max_outdoor_temp | - | - | YES | YES | YES | YES | YES
| Update mode | R/W | Holding register | 33 | val_u1 | 0 Dont allow from mobile app 1 Enabled 2 Disabled entirely | update_ctrl.update_mode | - | - | - | YES | YES | YES | YES
| Heating/Cooling mode BMS override | R/W | Holding register | 34 | val_u1 | Note: Only available in hardware profiles, which support manual H/C change-over. In other profiles override is set to DISABLED. 0 - DISABLED 1 - HEATING MODE 2 - COOLING MODE 3 - H/C MODE SET BY EXTERNAL SWITCH (only when HW input is available) | location.hc_mode_priority location.hc_mode_bms_override location.hc_mode_hw_source | - | - | - | - | YES | YES | YES
| Timezone number | R/W | Holding register | 35 | val_u2 | For list of supported timezones see tab "Timezone list" | - | - | - | - | - | YES | YES | YES
ROOMS (INDOOR ZONES)
Room 1 |  |  |  | 001xx
ROOM TYPE | Note: Dummy room is special type of room, where no thermostat or sensor is installed. Dummy room does not support cooling mode. To find out room type, check input register 127. | [6 empty] | - | - | - | - | YES | YES | YES
NORMAL, DUMMY | Aggregated warning | R | Discrete Inputs | 101 |  | A problem is pending in Room | - | YES | YES | YES | YES | YES | YES | YES
NORMAL, DUMMY | Aggregated error | R | Discrete Inputs | 102 |  | A critical problem is pending in Room | - | YES | YES | YES | YES | YES | YES | YES
NORMAL | Warning - low battery | R | Discrete Inputs | 103 |  | There are one or more peripherals in the room with low battery. | room.warn_periph_low_batery | YES | YES | YES | YES | YES | YES | YES
NORMAL | Error - peripheral lost | R | Discrete Inputs | 104 |  | There are one or more peripherals in the room which are not responding. | room.alarm_periph_unreachable | YES | YES | YES | YES | YES | YES | YES
[12 empty] | YES | YES | YES
NORMAL, DUMMY | Desired temp | R | Input Register | 101 | val_d2_fp100 | Shows the desired temperature in the room. | room.tmp_ctrl.temp_desired | YES | YES | YES | YES | YES | YES | YES
NORMAL, DUMMY | General Heating/Cooling state (radiator ¦ underfloor ¦ integration) | R | Input Register | 102 | val_u1 | 1 IDLE 2 HEATING 3 COOLING 4 BLOCKED_HEATING 5 BLOCKED_COOLING | room.tmp_ctrl.state room.tmp_ctrl.blocking | YES | YES | EXTENDED | YES | YES | YES | YES
NORMAL, DUMMY | General Heating/Cooling blocking source (radiator ¦ underfloor ¦ integration) | R | Input Register | 103 | val_u1 | Please check top of the document - GENERAL BLOCKING SOURCES | room.tmp_ctrl.blocking | YES | YES | EXTENDED | YES | YES | YES | YES
NORMAL | Air temperature | R | Input Register | 104 | val_d2_fp100 | Current air temperature measured in the room. | room.air_temp | YES | YES | YES | YES | YES | YES | YES
NORMAL | Floor temperature | R | Input Register | 105 | val_d2_fp100 | Current floor temperature measured in the room. | room.floor_temp | YES | YES | YES | YES | YES | YES | YES
NORMAL | Relative humidity | R | Input Register | 106 | val_d2_fp100 | Current humidity measured in the room. | room.humidity | YES | YES | YES | YES | YES | YES | YES
NORMAL | Calculated dew point | R | Input Register | 107 | val_d2_fp100 | Current calculated dewpoint | room.dew_point | - | - | YES | YES | YES | YES | YES
NORMAL | CO concentration | R | Input Register | 108 | reserved | reserved | reserved | - | - | - | - | - | - | - | BLOCKED .. waits for sensor
NORMAL | CO2 concentration | R | Input Register | 109 | val_u2 | Current CO2 concentration in ppm | room.co2_level | - | - | - | - | - | - | YES
NORMAL | VOC concentration | R | Input Register | 110 | val_u2 | Current VOC concentration in VOC index | room.voc_level | - | - | - | - | - | - | YES
NORMAL | Associated to Radiators | R | Input Register | 111 | val_u1 | 0 .. NONE 73 .. ITC1 (Address of modbus object) 74 .. ITC2 (Address of modbus object) 77 .. HCC1 (Address of modbus object) 78 .. HCC2 (Address of modbus object) 79 .. HCC3 (Address of modbus object) 81 .. H/C Source (Address of modbus object) | room.air_hcw_ctrl.supplier_oid | - | - | YES | CHANGED | YES | YES | YES
NORMAL | Associated to UFHC | R | Input Register | 112 | val_u1 | 0 .. NONE 73 .. ITC1 (Address of modbus object) 74 .. ITC2 (Address of modbus object) 77 .. HCC1 (Address of modbus object) 78 .. HCC2 (Address of modbus object) 79 .. HCC3 (Address of modbus object) | room.ufhc_hcw_ctrl.hcw_supplier_oid | - | - | YES | CHANGED | YES | YES | YES
NORMAL | Associated to Heating block (logical) - reserved | R | Input Register | 113 | val_u1 |  |  | - | - | - | - | - | - | -
NORMAL | Associated to Drying (humidity control) | R | Input Register | 114 | val_u1 | 0 .. NONE 650 .. DEHUM 1 (Address of modbus object) 651 .. DEHUM 2 (Address of modbus object) 652 .. DEHUM 3 (Address of modbus object) 653 .. DEHUM 4 (Address of modbus object) | room.hum_ctrl.drying_supplier_oid | - | - | - | YES | YES | YES | YES
NORMAL | Associated to Thermal integration (thermal. integ control) | R | Input Register | 115 | val_u1 | 0 .. NONE 650 .. DEHUM 1 (Address of modbus object) 651 .. DEHUM 2 (Address of modbus object) 652 .. DEHUM 3 (Address of modbus object) 653 .. DEHUM 4 (Address of modbus object) | room.ti_ctrl.integration_supplier_oid | - | - | - | YES | YES | YES | YES
NORMAL | Associated to Ventilation (air quality control) | R | Input Register | 116 | val_u1 | 0 .. NONE 610 .. Ventilation 1 (Address of modbus object) 611 .. Ventilation 2 (Address of modbus object) | room.ventilation_ctrl.ventilation_supplier_oid | - | - | - | - | - | YES | YES
NORMAL | Radiators state (air temperature) | R | Input Register | 117 | val_u1 | 0 NONE (not used in this room or load was not detected on at least one output) 1 IDLE 2 HEATING 3 COOLING 4 BLOCKED_HEATING 5 BLOCKED_COOLING | room.tmp_ctrl.radiator_state | - | - | - | YES | YES | YES | YES
NORMAL | Underfloor Heating/Cooling state (floor temperature) | R | Input Register | 118 | val_u1 | 0 NONE (not used in this room or load was not detected on at least one output) 1 IDLE 2 HEATING 3 COOLING 4 BLOCKED_HEATING 5 BLOCKED_COOLING | room.tmp_ctrl.floor_state | - | - | - | YES | YES | YES | YES
NORMAL | Drying state (relative humidity) | R | Input Register | 119 | val_u1 | 0 NONE (not used in this room) 1 IDLE 2 DRYING 3 BLOCKED_DRYING | room.hum_ctrl.drying_state | - | - | - | YES | YES | YES | YES
NORMAL | Thermal integration state (air temperature) | R | Input Register | 120 | val_u1 | 0 NONE (not used in this room) 1 IDLE 2 HEATING 3 COOLING 4 BLOCKED_HEATING 5 BLOCKED_COOLING | room.ti_ctrl.integration_state | - | - | - | YES | YES | YES | YES
NORMAL | Ventilation state | R | Input Register | 121 | val_u1 | 0 NONE (not used in this room) 1 STOPPED 2 UNOCCUPIED 3 ECONOMY 4 COMFORT 5 BOOST 6 BLOCKED | room.ventilation_ctrl.state.state room.ventilation_ctrl.state.blocking | - | - | - | - | - | YES | YES
NORMAL | Blocking source - Radiators | R | Input Register | 122 | val_u1 | Same as Heating/Cooling blocking source | room.tmp_ctrl.radiator_blocking | - | - | - | YES | YES | YES | YES
NORMAL | Blocking source - Underfloor Heating/Cooling | R | Input Register | 123 | val_u1 | Same as Heating/Cooling blocking source | room.tmp_ctrl.floor_blocking | - | - | - | YES | YES | YES | YES
NORMAL | Blocking source - Drying | R | Input Register | 124 | val_u1 | Same as Heating/Cooling blocking source | room.hum_ctrl.drying_blocking | - | - | - | YES | YES | YES | YES
NORMAL | Blocking source - Integration | R | Input Register | 125 | val_u1 | Same as Heating/Cooling blocking source | room.ti_ctrl.integration_blocking | - | - | - | YES | YES | YES | YES
NORMAL | Blocking source - Ventilation | R | Input Register | 126 | val_u1 | Same as Heating/Cooling blocking source | room.ventilation_ctrl.state.blocking | - | - | - | - | - | YES | YES
NORMAL, DUMMY | Room type | R | Input Register | 127 | val_u1 | 0 - NORMAL (DEFAULT) 1 - DUMMY (no thermostat or sensor installed) | room.object_info.subtype | - | - | - | - | YES | YES | YES
DUMMY | Associated Heating Source | R | Input Register | 128 | val_u1 | 0 .. NONE 73 .. ITC1 (Address of modbus object) 74 .. ITC2 (Address of modbus object) 77 .. HCC1 (Address of modbus object) 78 .. HCC2 (Address of modbus object) 79 .. HCC3 (Address of modbus object) 81 .. H/C Source (Address of modbus object) | room.air_hcw_ctrl.supplier_oid room.ufhc_hcw_ctrl.hcw_supplier_oid | - | - | - | - | YES | YES | YES
NORMAL, DUMMY | Room name | R/W | Holding register | 00101 - 00116 | val_utf8 | String description (32 Bytes, UTF8, NULL terminated) | room.name | YES | FORMAT CHANGED | YES | YES | YES | YES | YES
NORMAL, DUMMY | Room mode | R/W | Holding register | 117 | val_u1 | 0 SCHEDULE 1 MANUAL In SCHEDULE mode, the “Room temperature setpoint” is not used and the room temperature is controlled by scheduler. | room.mode | YES | YES | YES | YES | YES | YES | YES
NORMAL, DUMMY | Room mode override | R/W | Holding register | 118 | val_u1 | 0 NONE 1 TEMPORARY 2 VACATION_AWAY 3 ADJUST NORMAL ROOM: In override mode (> NONE), the “Room temperaturesetpoint” is not used. The requested temperature is corrected by user via room thermostat or mobile application. You can disable the override mode by setting this value to 0 (NONE) DUMMY ROOM: In override mode (> NONE), the “Room temperature preset” is not used. The requested temperature preset is changed by user via LCD or mobile application. You can disable the override mode by setting this value to 0 (NONE) | room.mode_override |  | YES | YES | YES | YES | YES | YES
NORMAL | Room temperature setpoint | R/W | Holding register | 119 | val_d2_fp100 | Temperature requested by user. This values is not used when - Room mode = SCHEDULE (Scheduler temperature is used) - Location.Vacation = ON (Vacation temperature is used) - Location.Standby = ON (Standby temperature is used) - Temporary mode is activated (User defined temperature is used) | room.tmp_ctrl.heat.temp_set_manual room.tmp_ctrl.cool.temp_set_manual | YES | YES | YES | YES | YES | YES | YES
NORMAL | User Interface access level (thermostat lock) | R/W | Holding Register | 120 | val_u1 | 8 LOCKED (Read Only) 16 HOTEL 32 UNLOCKED | room.therm_access_level | - | - | YES | YES | YES | YES | YES
NORMAL, DUMMY | Standby temperature | R/W | Holding Register | 121 | val_d2_fp100 | Room temperature setpoint used when the system is in Standby mode | room.tmp_ctrl.heat.temp_set_standby room.tmp_ctrl.cool.temp_set_standby | - | - | YES | YES | YES | YES | YES
NORMAL, DUMMY | Vacation temperature | R/W | Holding Register | 122 | val_d2_fp100 | Room temperature setpoint used when the system is in Vacation mode | room.tmp_ctrl.heat.temp_set_vacation room.tmp_ctrl.cool.temp_set_vacation | - | - | YES | YES | YES | YES | YES
NORMAL, DUMMY | Exclude from vacation | R/W | Holding Register | 123 | val_u1 | Do not allow the Vacation mode in this room | room.allow_vacation_away | - | - | YES | YES | YES | YES | YES
NORMAL | Adaptive mode | R/W | Holding Register | 124 | val_u1 | Allow adaptive mode | room.tmp_ctrl.adaptive_mode_ena | - | - | YES | YES | YES | YES | YES
NORMAL | Thermal integration heating offset | R/W | Holding Register | 125 | val_d2_fp100 | Thermal integration heating offset | room.ti_ctrl.offset | - | - | - | YES | YES | YES | YES
NORMAL | Thermal integration hysteresis | R/W | Holding Register | 126 | val_d2_fp100 | Thermal integration hysteresis | room.ti_ctrl.hysteresis | - | - | - | YES | YES | YES | YES
NORMAL | Humidity threshold heating | R/W | Holding Register | 127 | val_d2_fp100 | Humidity threshold heating | room.hum_ctrl.heat.hum_set_manual | - | - | - | YES | YES | YES | YES
NORMAL | Humidity threshold cooling | R/W | Holding Register | 128 | val_d2_fp100 | Humidity threshold cooling | room.hum_ctrl.cool.hum_set_manual | - | - | - | YES | YES | YES | YES
NORMAL | Humidity hysteresis | R/W | Holding Register | 129 | val_d2_fp100 | Humidity hysteresis | room.hum_ctrl.hum_hysteresis | - | - | - | YES | YES | YES | YES
NORMAL | Drying - cooling water offset | R/W | Holding Register | 130 | val_d2_fp100 | Drying - cooling water offset | room.hum_ctrl.cool.drying_offset | - | - | - | YES | YES | YES | YES
NORMAL | Drying - cooling water offset hysteresis | R/W | Holding Register | 131 | val_d2_fp100 | Drying - cooling water offset hysteresis | room.hum_ctrl.drying_offset_hysteresis | - | - | - | YES | YES | YES | YES
NORMAL | Dew point cooling threshold | R/W | Holding Register | 132 | val_d2_fp100 | Dew point threshold temp when cooling | room.hum_ctrl.drying_on_cooling_dew_point_threshold | - | - | - | YES | YES | YES | YES
NORMAL | Dew point cooling threshold hysteresis | R/W | Holding Register | 133 | val_d2_fp100 | Dew point threshold temp hysteresis when cooling | room.hum_ctrl.drying_on_cooling_dew_point_hysteresis | - | - | - | YES | YES | YES | YES
NORMAL | Humidity high alarm limit | R/W | Holding Register | 134 | val_d2_fp100 | Humidity high alarm limit | room.hum_ctrl.hum_alarm_high | - | - | - | YES | YES | YES | YES
DUMMY | Room temperature preset | R/W | Holding register | 135 | val_u1 | 0 - ECO 1 - COMFORT 2 - EXTRA COMFORT Temperature preset requested by user. This value is not used when - Room mode = SCHEDULE (Scheduler temperature is used) - Location.Vacation = ON (Vacation temperature is used) - Location.Standby = ON (Standby temperature is used) - Temporary mode is activated (User defined temperature is used) | room.tmp_ctrl.heat.temp_set_eco room.tmp_ctrl.heat.temp_set_comfort room.tmp_ctrl.heat.temp_set_extra_comfort | - | - | - | - | YES | YES | YES
Room 2 | Same as Room 1 |  |  | 002xx
Room 3 | Same as Room 1 |  |  | 003xx
… |  |  |  | …
Room 16 | Same as Room 1 |  |  | 016xx
Reserved for more rooms |  |  |  | 017xx-032xx
OUTDOOR ZONES
Outdoor 1 |  |  |  | 033xx
| Aggregated warning | R | Discrete Inputs | 3301 |  | A problem is pending in Outdoor zone | - | YES | YES | YES | YES | YES | YES | YES
| Aggregated error | R | Discrete Inputs | 3302 |  | A critical problem is pending in Outdoor zone | - | YES | YES | YES | YES | YES | YES | YES
| Warning - low battery | R | Discrete Inputs | 3303 |  | There are one or more peripherals in the Outdoor zone with low battery. | device.warn_periph_low_batery | YES | YES | YES | YES | YES | YES | YES
| Error - peripheral lost | R | Discrete Inputs | 3304 |  | There are one or more peripherals in the Outdoor zone which are not responding. | device.warn_periph_unreachable | YES | YES | YES | YES | YES | YES | YES
| Air Temp | R | Input Register | 3301 | val_d2_fp100 | Used in H/C mode switching, H/C blocking | outdoor.outdoor_temp | - | YES | YES | YES | YES | YES | YES
| Air Temp Filtered | R | Input Register | 3302 | val_d2_fp100 | Used in heat curve calculations, frost protection | outdoor.filtered_outdoor_temp | - | YES | YES | YES | YES | YES | YES
| Air Temp Geometrical | R | Input Register | 3303 | val_d2_fp100 | Not yet used | outdoor.average_outdoor_temp | - | YES | YES | YES | YES | YES | YES
| Air humidity | R | Input Register | - |  |  |  | - | - | - | - | - | - | - | BLOCKED .. no sensor
| Air CO2 | R | Input Register | - |  |  |  | - | - | - | - | - | - | - | BLOCKED .. no sensor
| Light level | R | Input Register | - |  |  |  | - | - | - | - | - | - | - | BLOCKED .. no sensor
| Name | R | Holding Register | 03301 - 03316 | val_utf8 | String description (32 Bytes, UTF8, NULL terminated) | Read only, fixed name "outdoor" | - | YES | YES | YES | YES | YES | YES
| Air Temp BMS Override | R/W | Holding Register | 3317 | val_d2_fp100 | Overrides Air Temp value (register 03301). Invalid value (327,67) means override is disabled. | outdoor.outdoor_temp_bms_override | - | YES | YES | YES | YES | YES | YES
Reserved | For Outdoor zones 3-4 |  |  | 034xx-036xx | [10 empty] | BLOCKED .. waits for architecture
Reserved | For other types of zones |  |  | 037xx-064xx
DHW CONTROLLERS
DHW 201 |  |  |  | 065xx
| Aggregated warning | R | Discrete Inputs | 6501 |  | A problem is pending in DHW | - | YES | YES | YES | YES | YES | YES | YES
| Aggregated error | R | Discrete Inputs | 6502 |  | A critical problem is pending in DHW | - | YES | YES | YES | YES | YES | YES | YES
| Warning - Retentive Low Energy | R | Discrete Inputs | 6503 |  |  | dhw.calefa_ctrl.warn_low_energy | YES | YES | YES | YES | YES | YES | YES
| Error - DHW temp high | R | Discrete Inputs | 6504 |  |  | dhw.calefa_ctrl.alarm_high_temp | YES | YES | YES | YES | YES | YES | YES
| Error - Motor failure | R | Discrete Inputs | 6505 |  |  | dhw.calefa_ctrl. alarm_motor_fail | YES | YES | YES | YES | YES | YES | YES
| Error - DHI sensor failure (source inlet) | R | Discrete Inputs | 6506 |  |  | dhw.calefa_ctrl. alarm_dhi_sensor_fail | YES | YES | YES | YES | YES | YES | YES
| Error - DHO sensor failure (source return) | R | Discrete Inputs | 6507 |  |  | dhw.calefa_ctrl. alarm_dho_sensor_fail | YES | YES | YES | YES | YES | YES | YES
| Error - DHW sensor failure | R | Discrete Inputs | 6508 |  |  | dhw.calefa_ctrl. alarm_dhw_sensor_fail | YES | YES | YES | YES | YES | YES | YES
| Error - DCW sensor failure | R | Discrete Inputs | 6509 |  |  | dhw.calefa_ctrl. alarm_dcw_sensor_fail | YES | YES | YES | YES | YES | YES | YES
| Warning - Pressure high | R | Discrete Inputs | 6510 |  |  | dhw.calefa_ctrl. warn_press_high | - | - | YES | YES | YES | YES | YES
| Warning - Pressure low | R | Discrete Inputs | 6511 |  |  | dhw.calefa_ctrl. warn_press_low | - | - | YES | YES | YES | YES | YES
| Error - Pressure critical low | R | Discrete Inputs | 6512 |  |  | dhw.calefa_ctrl. alarm_press_crit_low | - | - | YES | YES | YES | YES | YES
| Error - flow sensor failure | R | Discrete Inputs | 6513 |  |  | dhw.calefa_ctrl.alarm_flowsensor_fail | - | - | - | - | YES | YES | YES
| Desired DHW temp | R | Input Register | 6501 | val_d2_fp100 | Shows the desired temperature of the domestic hot water. | dhw. calefa_ctrl.temp_set | YES | YES | YES | YES | YES | YES | YES
| State | R | Input Register | 6502 | val_u1 | 1 IDLE 2 HEATING (hot water is consumed by user) 3 BYPASS (keeping heat exchanger hot for circulation) 4 BLOCKED_HEATING 5 BLOCKED_BYPASS Shows, whether the system wants to heat or to have bypass activated. | dhw.state dhw.blocking | YES | YES | CHANGED | YES | YES | YES | YES
| Blocking source | R | Input Register | 6503 | val_u1 | Please check top of the document - GENERAL BLOCKING SOURCES | dhw.blocking | YES | YES | YES | YES | YES | YES | YES
| Circulation state | R | Input Register | 6504 | val_u1 | 0 NONE (disabled) 1 IDLE 2 ON | dhw.circ_ctrl.circ_state dhw.circ_ctrl.circ_pump_present | YES | YES | CHANGED | YES | YES | YES | YES
| Measured DHW temp | R | Input Register | 6505 | val_d2_fp100 | Current temperature of the domestic hot water flowing from DHW | dhw.calefa_ctrl.dhw_temp | - | - | YES | YES | YES | YES | YES
| Source - Inlet temp | R | Input Register | 6506 | val_d2_fp100 | Current temperature of the water incoming from the heat source. | dhw.calefa_ctrl.hcw_source_inlet_temp | - | - | YES | YES | YES | YES | YES
| Source - Return temp | R | Input Register | 6507 | val_d2_fp100 | Current temperature of the water returning to the heat source. | dhw.calefa_ctrl.hcw_source_return_temp | - | - | YES | YES | YES | YES | YES
| Pressure | R | Input Register | 6508 | val_d2_fp100 | Current pressure of the secondary system | dhw.calefa_ctrl.hcw_pressure | - | - | YES | YES | YES | YES | YES
| Domestic Cold Water Temp | R | Input Register | 6509 | val_d2_fp100 | On heat exchanger input | dhw.calefa_ctrl.dcw_temp | - | - | - | YES | YES | YES | YES
| Domestic Cold Water flow | R | Input Register | 6510 | val_d2 | flow meter (analog) in l/h | dhw.calefa_ctrl.dcw_flow | - | - | - | YES | YES | YES | YES
| Valve position | R | Input Register | 6511 | val_d2_fp100 | Valve position in flows | dhw.calefa_ctrl.source_valve_level | - | - | - | - | YES | YES | YES
| Boost pump state | R | Input Register | 6512 | val_u1 | Boost pump state 0 IDLE 1 ON | dhw.boost_state | - | - | - | - | YES | YES | YES
NON PUBLIC | HOT_Working_point | R | Input Register | 6589 | val_d2 | Hot regulator - Calculated working point | device.reg_vals.hot_working_point | - | - | - | - | YES | YES | YES
NON PUBLIC | HOT_Low_energy_offset_value | R | Input Register | 6590 | val_d2 | Hot regulator - Low energy offset value | device.reg_vals.low_energy_offset | - | - | - | - | YES | YES | YES
NON PUBLIC | HOT_P_Val | R | Input Register | 6591 | val_d2 | Hot regulator - PID P value | device.reg_vals.hot_TMP_Pval | - | - | - | - | YES | YES | YES
NON PUBLIC | HOT_I_Val | R | Input Register | 6592 | val_d2 | Hot regulator - PID I value | device.reg_vals.hot_TMP_I_fil | - | - | - | - | YES | YES | YES
NON PUBLIC | HOT_D_Val | R | Input Register | 6593 | val_d2 | Hot regulator - PID D value | device.reg_vals.hot_TMP_DVal | - | - | - | - | YES | YES | YES
NON PUBLIC | HOT_HEX_D_Val | R | Input Register | 6594 | val_d2 | Hot regulator - HEX_D value | device.reg_vals.HEX_Dval | - | - | - | - | YES | YES | YES
NON PUBLIC | HEX factor | R | Input Register | 6595 | val_d2 | HEX factor | device.get_hex_factor | - | - | - | - | YES | YES | YES
NON PUBLIC | System mode | R | Input Register | 6596 | val_u2 | System mode 0 SYSTEM_MODE_RESET 1 SYSTEM_MODE_CALIBRATION 2 SYSTEM_MODE_RUN 3 SYSTEM_MODE_HEX_SENSE 4 SYSTEM_MODE_OVERRIDE 5 SYSTEM_MODE_VALVE_EXERCISE 6 SYSTEM_MODE_REBOOT 7 SYSTEM_MODE_UPGRADE | device.device_status.system_mode | - | - | - | - | YES | YES | YES
NON PUBLIC |  | R | Input Register | 6597 | val_u2 | Unused |  | - | - | - | - | - | - | -
NON PUBLIC | Motor position | R | Input Register | 6598 | val_d2 | Motor position in steps | device.sapi.steps_actual | - | - | - | - | YES | YES | YES
NON PUBLIC | Regulator state extended | R | Input Register | 6599 | val_u2 | Regulator state extended (including sub-states) 0 REG_STATE_EXT_Q0_STANDBY 1 REG_STATE_EXT_Q1_COLD_ALL_IN 2 REG_STATE_EXT_Q2_COLD_ALL_IN_BOOST 3 REG_STATE_EXT_Q3_COLD_PD 4 REG_STATE_EXT_Q4_COLD_PD_BOOST 5 REG_STATE_EXT_Q5_HOT 6 REG_STATE_EXT_Q6_HOT_BOOST 7 REG_STATE_EXT_Q7_HOT_OFFSET 8 REG_STATE_EXT_Q8_BYPASS 9 REG_STATE_EXT_Q9_PANIC 10 REG_STATE_EXT_Q10_FROST_PROTECT 15 REG_STATE_EXT_Q15_SHUTDOWN 99 REG_STATE_EXT_Q99_FAIL 255 REG_STATE_EXT_UNKNOWN | dhw_reg.regulator_get_state_ext | - | - | - | - | YES | YES | YES
| Name | R/W | Holding Register | 06501 - 06516 | val_utf8 | String description (32 Bytes, UTF8, NULL terminated) | dhw.name | YES | FORMAT CHANGED | YES | YES | YES | YES | YES
| Mode | R/W | Holding Register | 6517 | val_u1 | 0 SCHEDULE 1 SCHEDULE_ADAPTIVE 2 ECO 3 COMFORT Eco = circulation and hot bypass are disabled Comfort = circulation and hot bypass are enabled | dhw.mode | YES | YES | YES | YES | YES | YES | YES
| User interface access level (calefa display lock) | R/W | Holding Register | 6518 | val_u1 | < 40 USER (user menu) >= 40 INSTALLER (inst. menu) | dhw.access_level | YES | YES | YES | YES | YES | YES | YES
| Block request | R/W | Holding Register | 6519 | val_u1 | 0 NONE 1 BLOCK_REQUEST When BLOCK_REQUEST is set, then the system blocks heating and bypass to eliminate consumption from heat supplier. | dhw. calefa_ctrl.block_by_bms | YES | YES | YES | YES | YES | YES | YES
| Power consumption limit | R/W | Holding Register | 6520 | val_u2 |  | dhw. calefa_ctrl.pwr_consumption_limit | YES | YES | YES | YES | YES | YES | YES
| DHW temp set | R/W | Holding Register | 6521 | val_d2_fp100 | Requested temperature of domestic hot water. | dhw. calefa_ctrl.temp_set | YES | YES | YES | YES | YES | YES | YES
| DHW bypass temp | R/W | Holding Register | 6522 | val_d2_fp100 |  | dhw. calefa_ctrl.bypass_temp_set | YES | YES | YES | YES | YES | YES | YES
| Circulation - Pump present | R/W | Holding Register | 6523 | val_u1 | 0 DISABLED 1 ENABLED (scheduler) | dhw.circ_ctrl.circ_pump_present | YES | YES | YES | YES | YES | YES | YES
| Circulation - Inlet temp | R/W | Holding Register | 6524 | val_d2_fp100 | When circulation is enabled and there is NO dhw consumption, then the DHW temperature is regulated to this value. | dhw.circ_ctrl. circ_temp_set | YES | YES | YES | YES | YES | YES | YES
| Exclude from vacation | R/W | Holding Register | 6525 | val_u1 | Do not allow the Vacation mode | dhw.allow_vacation_away | - | - | YES | YES | YES | YES | YES
| Exclude from standby | R/W | Holding Register | 6526 | val_u1 | Do not allow the Standby mode | dhw.allow_standby | - | - | YES | YES | YES | YES | YES
| Boost pump mode | R/W | Holding Register | 6527 | val_u1 | Boost pump mode 0 OFF 1 LOW 2 HIGH | dhw.boost_mode | - | - | - | - | YES | YES | YES
YES
YES
NON PUBLIC | Testing support command | R/W | Holding Register | 6599 | val_u2 | Write test number to be executed. Reading this register will return either number of last/running test OR test result. Test result have following format: Higher byte - test number (e.g. 30 for buttons test) Lower byte - test result (depends on test number) 0 DISABLED 10 FAST_PUBLISH_ENABLE (publish every second) 20 DISPLAY_BLACK 21 DISPLAY_CLEAR 30 BUTTONS_TEST_START Starts buttons test for 10 seconds. After 10 seconds test result is available. Result format: - Higher byte = 30 - Lower byte = bit mask. 0 - button FAILED, 1 - button OK Bit 0 - button down Bit 1 - button up Bit 2 - button enter 40 RESET SETTINGS TO DEFAULT AND REBOOT Network mode is set to Modbus mode 50 START HEX CALIBRATION Switches system mode to SYSTEM_MODE_HEX_SENSE calibration. Result format: - Higher byte = 50 - Lower byte = enum seek_state 0 SEEK_STATE_INIT 1 SEEK_STATE_flowSTART 2 SEEK_STATE_COLDSTART 3 SEEK_STATE_COOLDOWN 4 SEEK_STATE_STABILIZE 5 SEEK_STATE_GET_WP 6 SEEK_STATE_DONE 7 SEEK_STATE_ABORT |  | - | - | - | - | YES | YES | YES
DHW Tank |  |  |  | 6600
| Aggregated warning | R | Discrete Inputs | 6601 |  | A problem is pending in DHW | - | - | - | YES | YES | YES | YES | YES
| Aggregated error | R | Discrete Inputs | 6602 |  | A critical problem is pending in DHW | - | - | - | YES | YES | YES | YES | YES
| Warning - cleaning process fail | R | Discrete Inputs | 6603 |  |  | dhw.tank_ctrl.warn_cleaning_fail | - | - | YES | YES | YES | YES | YES
| Error - Tank temp sensor fail | R | Discrete Inputs | 6604 |  |  | dhw.tank_ctrl.err_tank_sensor_fail | - | - | YES | YES | YES | YES | YES
| Error - Circulation return temp sensor fail | R | Discrete Inputs | 6605 |  |  | dhw.tank_ctrl.err_circ_sensor_fail | - | - | YES | YES | YES | YES | YES
| Error - Source return temp sensor fail | R | Discrete Inputs | 6606 |  |  | dhw.tank_ctrl.err_hcw_return_sensor_fail | - | - | YES | YES | YES | YES | YES
| Error - Source inlet temp sensor fail | R | Discrete Inputs | 6607 |  |  | dhw.tank_ctrl.err_hcw_inlet_sensor_fail | - | - | YES | YES | YES | YES | YES
| Warning - Source inlet temp too low | R | Discrete Inputs | 6608 |  |  | dhw.tank_ctrl.warn_low_hcw_source_temp | - | - | YES | YES | YES | YES | YES
| Warning - Peripheral low battery | R | Discrete Inputs | 6609 |  |  | dhw.tank_ctrl.warn_periph_low_battery | - | - | YES | YES | YES | YES | YES
| Error - Peripheral unreachable | R | Discrete Inputs | 6610 |  |  | dhw.tank_ctrl.err_periph_unreachable | - | - | YES | YES | YES | YES | YES
YES
| Tank - Measured temp | R | Input Register | 6601 | val_d2_fp100 | Current temperature of the domestic hot water in the tank | dhw.tank_ctrl.tank_temp | - | - | YES | YES | YES | YES | YES
| Tank - Desired temp | R | Input Register | 6602 | val_d2_fp100 | Desired temperature of the domestic hot water inside the tank (according to sheduler or manual setup). NOTE: The tank temperature is different form the temperature flowing from the tip. | dhw.tank_ctrl.temp_desired | - | - | YES | YES | YES | YES | YES
| Tank - State | R | Input Register | 6603 | val_u1 | 1 IDLE 2 HEATING 3 CLEANING 4 BLOCKED_HEATING 5 BLOCKED_CLEANING | dhw.state dhw.blocking | - | - | YES | YES | YES | YES | YES
| Tank - Blocking source | R | Input Register | 6604 | val_u1 | Please check top of the document - GENERAL BLOCKING SOURCES | dhw.blocking | - | - | YES | YES | YES | YES | YES
| Circulation - State | R | Input Register | 6605 | val_u1 | 0 NONE (disabled) 1 IDLE 2 ON | dhw.circ_ctrl.circ_state dhw.circ_ctrl.circ_pump_present | - | - | YES | YES | YES | YES | YES
| Circulation - Return temp | R | Input Register | 6606 | val_d2_fp100 | Current temperature of the domestic hot water returning from circulation. | dhw.circ_ctrl.circ_return_temp | - | - | YES | YES | YES | YES | YES
| Source - Inlet temp | R | Input Register | 6607 | val_d2_fp100 | Current temperature of the water incoming from the heat source. | dhw.tank_ctrl.hcw_source_inlet_temp | - | - | YES | YES | YES | YES | YES
| Source - Return temp | R | Input Register | 6608 | val_d2_fp100 | Current temperature of the water returning to the heat source. | dhw.tank_ctrl.hcw_source_return_temp | - | - | YES | YES | YES | YES | YES
| Name | R/W | Holding Register | 06601 - 06616 | val_utf8 | String description (32 Bytes, UTF8, NULL terminated) | dhw.name | - | - | YES | YES | YES | YES | YES
| Mode | R/W | Holding Register | 6617 | val_u1 | 0 SCHEDULE 2 ECO Eco = Circulation is disabled | dhw.circ_ctrl.circ_pump_present | - | - | YES | YES | YES | YES | YES
| Circulation - Cooldown time | R/W | Holding Register | 6618 | val_u2 | How long the circulation is supressed after is paused due to "Stop temp difference" | dhw.circ_ctrl.circ_cooldown_time | - | - | YES | YES | YES | YES | YES
| Circulation - Stop temp difference | R/W | Holding Register | 6619 | val_d2_fp100 | When difference between tank temperature and return temperature from circulation is lower than this value, the circulation pump is switched off. | dhw.circ_ctrl.circ_temp_difference | - | - | YES | YES | YES | YES | YES
| Source - Return temp limit | R/W | Holding Register | 6620 | val_d2_fp100 | The controller limits the source return temperature according to this value. (used only in "advanced tank mode") | dhw.tank_ctrl.hcw_source_return_temp_limit | - | - | YES | YES | YES | YES | YES
| Tank - Temp set | R/W | Holding Register | 6621 | val_d2_fp100 | Requested temperature of domestic hot water. | dhw. tank_ctrl.temp_set | - | - | YES | YES | YES | YES | YES
| Tank - Temp set vacation | R/W | Holding Register | 6622 | val_d2_fp100 | Requested temperature of domestic hot water in Vacation mode | dhw.tank_ctrl.temp_set_vacation | - | - | YES | YES | YES | YES | YES
| Tank - Temp set cleaning | R/W | Holding Register | 6623 | val_d2_fp100 | Requested temperature of domestic hot water during the cleaning process. | dhw.tank_ctrl.temp_set_cleaning | - | - | YES | YES | YES | YES | YES
| Tank - Temp set standby | R/W | Holding Register | 6624 | val_d2_fp100 | Requested temperature of domestic hot water in Standby mode | dhw.tank_ctrl.temp_set_standby | - | - | YES | YES | YES | YES | YES
| Exclude from vacation | R/W | Holding Register | 6625 | val_u1 | Do not allow the Vacation mode | dhw.allow_vacation_away | - | - | YES | YES | YES | YES | YES
| Exclude from standby | R/W | Holding Register | 6626 | val_u1 | Do not allow the Standby mode | dhw.allow_standby | - | - | YES | YES | YES | YES | YES
Reserved | For another types of DHW controllers (peripherals) |  |  | 067xx
CALEFA ITC CONTROLLERS
CALEFA ITC | Registers are same as SENTIO ITC |  |  | 068xx |  |  |  | - | - | - | - | - | YES | YES
Reserved | For another types of DHW controllers (peripherals) |  |  | 069xx-072xx
SENTIO ITC CONTROLLERS
SENTIO ITC1 |  |  |  | 073xx
| Aggregated warning | R | Discrete Inputs | 7301 |  | A problem is pending in ITC | - | - | - | YES | YES | YES | YES | YES
| Aggregated error | R | Discrete Inputs | 7302 |  | A critical problem is pending in ITC | - | - | - | YES | YES | YES | YES | YES
| Error - Inlet Sensor Failure | R | Discrete Inputs | 7303 |  | Missing or broken sensor | itc.err_inlet_sensor_fail | - | - | YES | YES | YES | YES | YES
| Error - Servo Failure | R | Discrete Inputs | 7304 |  | Missing or broken servo | itc.err_servo_fail | - | - | YES | YES | YES | YES | YES
| Error - Return Sensor Failure | R | Discrete Inputs | 7305 |  | Missing or broken sensor | itc.err_return_sensor_fail | - | - | YES | YES | YES | YES | YES
| Error - Outdoor Sensor Failure | R | Discrete Inputs | 7306 |  | Missing or broken sensor | itc.err_outdoor_sensor_fail | - | - | YES | YES | YES | YES | YES
| Error - High temp cut-off activated | R | Discrete Inputs | 7307 |  | Safety mechanism "high temp cut-off" is activated | itc.heat_ctrl.err_htco | - | - | YES | YES | YES | YES | YES
| Error - Frost protection activated | R | Discrete Inputs | 7308 |  | Safety mechanism "frost protection" is activated | itc.err_frost_protection_active | - | - | YES | YES | YES | YES | YES
YES
| State | R | Input Register | 7301 | val_u1 | 1 IDLE 2 HEATING 3 COOLING 4 BLOCKED_HEATING 5 BLOCKED_COOLING | itc.state itc.hcw_blocking | - | - | YES | YES | YES | YES | YES
| Blocking source | R | Input Register | 7302 | val_u1 | Please check top of the document - GENERAL BLOCKING SOURCES | itc.hcw_blocking | - | - | YES | YES | YES | YES | YES
| Pump - Demand | R | Input Register | 7303 | val_u1 | 1 IDLE 2 ON | itc.pump_demand | - | - | YES | YES | YES | YES | YES
| Pump - State | R | Input Register | 7304 | val_u1 | 1 IDLE 2 ON | itc.pump_state | - | - | YES | YES | YES | YES | YES
| Measured inlet temperature | R | Input Register | 7305 | val_d2_fp100 | Measured temperature of the inlet heating/cooling water. | itc.inlet_temp | - | - | YES | YES | YES | YES | YES
| Desired inlet temperature | R | Input Register | 7306 | val_d2_fp100 | Desired temperature of the inlet heating/cooling water. The value which the ITC regulator wants to meet. | itc.inlet_temp_desired | - | - | YES | YES | YES | YES | YES
| Measured return temperature | R | Input Register | 7307 | val_d2_fp100 | Measured return temperature | itc.return_temp | - | - | YES | YES | YES | YES | YES
| Main supplier temperature | R | Input Register | 7308 | val_d2_fp100 | Main supplier temperature | itc.hcw_supplier_oid.hcw_inlet_temp | - | - | - | YES | YES | YES | YES
| Servo position request [%] | R | Input Register | 7309 | val_d2_fp100 | Servo position request in percent | itc.servo_request | - | - | - | - | - | YES | YES
| Name | R/W | Holding Register | 07301-07316 | val_utf8 | String description (32 Bytes, UTF8, NULL terminated) | itc.name | - | - | YES | YES | YES | YES | YES
| Regulator - P value | R/W | Holding Register | 7317 | val_d2_fp10 | Proportional gain of temperature regulator | itc.heat_ctrl.itc_p_gain | - | - | YES | YES | YES | YES | YES
| Regulator - I value | R/W | Holding Register | 7318 | val_u2 | Integrating time of temperature regulator | itc.heat_ctrl.itc_i_time | - | - | YES | YES | YES | YES | YES
| Regulator - Hysteresis | R/W | Holding Register | 7319 | val_d2_fp100 | Hysteresis | itc.heat_ctrl.itc_hysteresis | - | - | YES | YES | YES | YES | YES
| Heat curve - type | R/W | Holding Register | 7320 | val_u1 | 0 MANUAL 1 CALCULATED 2 UNDERFLOOR 3 RADIATORS | itc.heat_ctrl.curve_type | - | - | YES | YES | YES | YES | YES
| Heat curve - manual slope | R/W | Holding Register | 7321 | val_d2_fp10 | Curve slope. Used only in MANUAL | itc.heat_ctrl.curve_manual | - | - | YES | YES | YES | YES | YES
| Heat curve - parallel displacement | R/W | Holding Register | 7322 | val_d2_fp100 | Shifts calculated temperature up/down | itc.heat_ctrl.curve_parallel_displacement | - | - | YES | YES | YES | YES | YES
| Heat curve - min inlet | R/W | Holding Register | 7323 | val_d2_fp100 | Lowest possible temperature | itc.heat_ctrl.curve_inlet_temp_min | - | - | YES | YES | YES | YES | YES
| Heat curve - max inlet | R/W | Holding Register | 7324 | val_d2_fp100 | Highest possible temperature | itc.heat_ctrl.curve_inlet_temp_max | - | - | YES | YES | YES | YES | YES
| Heat curve - gain | R/W | Holding Register | 7325 | val_d2_fp10 | Static gain of desired temperature calculation | itc.heat_ctrl.curve_no_ts_gain | - | - | YES | YES | YES | YES | YES
| Return temp limiter -function | R/W | Holding Register | 7326 | val_u1 | 0 OFF 1 MIN 2 MAX | itc.heat_ctrl.return_limiter_mode | - | - | YES | YES | YES | YES | YES
| Return temp max limiter - Limit | R/W | Holding Register | 7327 | val_d2_fp100 | Maximum allowed return temperature (limits inlet temperature) | itc.heat_ctrl.return_max_limit | - | - | YES | YES | YES | YES | YES
| Return temp max limiter - Gain | R/W | Holding Register | 7328 | val_d2_fp10 | Return limiter proportional gain. Use high value fast acting system, low value for slow acting system. | itc.heat_ctrl.return_max_limit_gain | - | - | YES | YES | YES | YES | YES
| Return temp max limiter - Priority over inlet | R/W | Holding Register | 7329 | val_u1 | 0 NO_PRIORITY 1 PRIORITY (return limiter can override "Heat curve - min inlet") | itc.heat_ctrl.return_max_limit_priority | - | - | YES | YES | YES | YES | YES
| Return temp min limiter - Limit | R/W | Holding Register | 7330 | val_d2_fp100 | Minimal allowed return temperature (limits inlet temperature) | itc.heat_ctrl.return_min_limit | - | - | YES | YES | YES | YES | YES
| Return temp min limiter - Gain | R/W | Holding Register | 7331 | val_d2_fp10 | Return limiter proportional gain. Use high value fast acting system, low value for slow acting system. | itc.heat_ctrl.return_min_limit_gain | - | - | YES | YES | YES | YES | YES
| Optimization - boost | R/W | Holding Register | 7332 | val_u1 | Boost desired temperature by "Optimization - boost flow" for 1 hour 0 DISABLED 1 ENABLED | itc.heat_ctrl.boost_mode | - | - | YES | YES | YES | YES | YES
| Optimization - boost flow | R/W | Holding Register | 7333 | val_u1 | Boost flow | itc.heat_ctrl.boost_level | - | - | YES | YES | YES | YES | YES
| Optimization - ramping | R/W | Holding Register | 7334 | val_u1 | Rise desired temperature over ramping time. 0 DISABLED 1 ENABLED | itc.heat_ctrl.ramping_mode | - | - | YES | YES | YES | YES | YES
| Optimization - ramping time | R/W | Holding Register | 7335 | val_u1 | Ramping time | itc.heat_ctrl.ramping_time | - | - | YES | YES | YES | YES | YES
| Frost protection - Mode | R/W | Holding Register | 7336 | val_u1 | Activate heating in assigned loops whe inlet temperature drops bellow "Frost protection - Temp" | itc.heat_ctrl.frost_protect_mode | - | - | YES | YES | YES | YES | YES
| Frost protection - Temp | R/W | Holding Register | 7337 | val_d2_fp100 | Frost protection limit | itc.heat_ctrl.frost_protect_temp | - | - | YES | YES | YES | YES | YES
| High Temp Cut-Off - Mode | R/W | Holding Register | 7338 | val_u1 | Heating is blocked, when inlet temperature exceeds the limit. Alarm is raised, pump is switched off (ignoring all pump delay). 0 DISABLED 1 ENABLED | itc.heat_ctrl.htco_mode | - | - | YES | YES | YES | YES | YES
| High Temp Cut-Off - Temp | R/W | Holding Register | 7339 | val_d2_fp100 | Limit temperature for High Temp Cut-Off | itc.heat_ctrl.htco_temp | - | - | YES | YES | YES | YES | YES
| Cooling Regulator - P value | R/W | Holding Register | 7340 | val_d2_fp10 | Proportional gain of temperature regulator in cooling mode | itc.cool_ctrl.cool_p_gain | - | - | - | YES | YES | YES | YES
| Cooling Regulator - I value | R/W | Holding Register | 7341 | val_u2 | Integrating time of temperature regulator in cooling mode | itc.cool_ctrl.cool_i_time | - | - | - | YES | YES | YES | YES
| Cooling Regulator - Hysteresis | R/W | Holding Register | 7342 | val_d2_fp100 | Hysteresis in cooling mode | itc.cool_ctrl.cool_hysteresis | - | - | - | YES | YES | YES | YES
| Cooling inlet temp min | R/W | Holding Register | 7343 | val_d2_fp100 | Lowest possible temperature in cooling mode | itc.cool_ctrl.cool_inlet_temp_min | - | - | - | YES | YES | YES | YES
| Cooling inlet temp max | R/W | Holding Register | 7344 | val_d2_fp100 | Highest possible temperature in cooling mode | itc.cool_ctrl.cool_inlet_temp_max | - | - | - | YES | YES | YES | YES
SENTIO ITC2 | Same as ITC1 |  |  | 074xx |  |  |  | - | - | YES | YES | YES | YES | YES
Reserved | For SENTIO ITC3, SENTIO ITC4 |  |  | 075xx-076xx
HCC CONTROLLERS
HCC1 |  |  |  | 077xx
| Aggregated warning | R | Discrete Inputs | 7701 |  | A problem is pending in ITC | - | - | YES | YES | YES | YES | YES | YES
| Aggregated error | R | Discrete Inputs | 7702 |  | A critical problem is pending in ITC | - | - | YES | YES | YES | YES | YES | YES
| Error - inlet sensor failure | R | Discrete Inputs | 7703 |  |  | hcc.err_inlet_sensor_fail | - | YES | YES | YES | YES | YES | YES
| Error - High temp cut-off activated | R | Discrete Inputs | 7704 |  | Safety mechanism "high temp cut-off" is activated | hcc.heat_ctrl.alarm_htco | - | YES | YES | YES | YES | YES | YES
YES
| State | R | Input Register | 7701 | val_u1 | 1 IDLE 2 HEATING 3 COOLING 4 BLOCKED_HEATING 5 BLOCKED_COOLING | hcc.state hcc.hcw_blocking | - | YES | CHANGED | YES | YES | YES | YES
| Blocking source | R | Input Register | 7702 | val_u1 | Please check top of the document - GENERAL BLOCKING SOURCES | hcc.hcw_blocking | - | YES | YES | YES | YES | YES | YES
| Pump - Demand | R | Input Register | 7703 | val_u1 | 1 IDLE 2 ON | hcc.pump_demand | - | YES | YES | YES | YES | YES | YES
| Pump - State | R | Input Register | 7704 | val_u1 | 1 IDLE 2 ON | hcc.pump_state | - | YES | YES | YES | YES | YES | YES
| Measured inlet temperature | R | Input Register | 7705 | val_d2_fp100 | Measured temperature of the inlet heating/cooling water. | hcc.inlet_temp | - | YES | YES | YES | YES | YES | YES
| Desired inlet temperature | R | Input Register | 7706 | val_d2_fp100 | Desired temperature of the inlet heating/cooling water. The value which the ITC regulator wants to meet. | hcc.hcw_required_temp | - | YES | YES | YES | YES | YES | YES
| Measured return temperature | R | Input Register | 7707 | val_d2_fp100 | Measured temperature of the return heating/cooling water. | hcc.return_temp | - | - | - | - | - | - | - | BLOCKED .. No sensor
| Name | R/W | Holding Register | 07701-07716 | val_utf8 | String description (32 Bytes, UTF8, NULL terminated) | hcc.name | - | YES | YES | YES | YES | YES | YES
| Heat curve - type | R/W | Holding Register | 7717 | val_u1 | 0 MANUAL 1 CALCULATED 2 UNDERFLOOR 3 RADIATORS | hcc.heat_ctrl.curve_type | - | YES | YES | YES | YES | YES | YES
| Heat curve - manual slope | R/W | Holding Register | 7718 | val_d2_fp10 | Curve slope. Used only in MANUAL | hcc.heat_ctrl.curve_manual | - | YES | YES | YES | YES | YES | YES
| Heat curve - parallel displacement | R/W | Holding Register | 7719 | val_d2_fp100 | Shifts calculated temperature up/down | hcc.heat_ctrl.curve_parallel_displacement | - | YES | YES | YES | YES | YES | YES
| Heat curve - min inlet | R/W | Holding Register | 7720 | val_d2_fp100 | Lowest possible temperature | hcc.heat_ctrl.curve_inlet_temp_min | - | YES | YES | YES | YES | YES | YES
| Heat curve - max inlet | R/W | Holding Register | 7721 | val_d2_fp100 | Highest possible temperature | hcc.heat_ctrl.curve_inlet_temp_max | - | YES | YES | YES | YES | YES | YES
| Heat curve - gain | R/W | Holding Register | 7722 | val_d2_fp10 | Static gain of desired temperature calculation | hcc.heat_ctrl.curve_no_ts_gain | - | YES | YES | YES | YES | YES | YES
| High Temp Cut-Off - Mode | R/W | Holding Register | 7723 | val_u1 | Heating is blocked, when inlet temperature exceeds the limit. Alarm is raised, pump is switched off (ignoring all pump delay). 0 DISABLED 1 ENABLED | hcc.heat_ctrl.htco_mode | - | YES | YES | YES | YES | YES | YES
| High Temp Cut-Off - Temp | R/W | Holding Register | 7724 | val_d2_fp100 | Limit temperature for High Temp Cut-Off | hcc.heat_ctrl.htco_temp hcc.heat_ctrl.htco_relative_temp | - | YES | YES | YES | YES | YES | YES
YES
HCC2 | same as HCC1 |  |  | 078xx |  |  |  | - | YES | YES | YES | YES | YES | YES
HCC3 | same as HCC1 |  |  | 079xx |  |  |  | - | - | - | YES | YES | YES | YES
Reserved | for HCC4 |  |  | 080xx
H/C Source
H/C Source
| Aggregated warning | R | Discrete Inputs | 8101 |  | A problem is pending in H/C Source | - | - | - | - | YES | YES | YES | YES
| Aggregated error | R | Discrete Inputs | 8102 |  | A critical problem is pending in H/C Source | - | - | - | - | YES | YES | YES | YES
| Error general failure | R | Discrete Inputs | 8103 |  | General failure | hcw.err_source_general_failure | - | - | - | YES | YES | YES | YES
YES
| State | R | Input Register | 8101 | val_u1 | 1 IDLE 2 HEATING 3 COOLING 4 BLOCKED_HEATING 5 BLOCKED_COOLING | hcw.hcw_status hcw.hcw_blocking | - | - | - | YES | YES | YES | YES
HCW Source Elements
Boiler/Heat Pump
| Aggregated warning | R | Discrete Inputs | 8201 |  | A problem is pending in Boiler/Heat Pump | - | - | - | - | - | - | - | YES
| Aggregated error | R | Discrete Inputs | 8202 |  | A critical problem is pending in Boiler/Heat Pump | - | - | - | - | - | - | - | YES
| Error - inlet temp sensor failure | R | Discrete Inputs | 8203 |  | Inlet temperature sensors failure | hcw_source.err_inlet_sensor_fail | - | - | - | - | - | - | YES
| Error - general failure | R | Discrete Inputs | 8204 |  | General failure | hcw_source_element.err_source_general_failure | - | - | - | - | - | - | YES
| State | R | Input Register | 8201 | val_u1 | 1 IDLE 2 HEATING_PREPARE 3 HEATING_ACTIVE 4 HEATING_TERMINATE 5 COOLING_PREPARE 6 COOLING_ACTIVE 7 COOLING_TERMINATE 8 BLOCKED_HEATING 9 BLOCKED_COOLING 10 FAILURE | hcw_source_element.hcws_element_status hcw_source_element.hcw_blocking | - | - | - | - | - | - | YES
| Blocking source | R | Input Register | 8202 | val_u1 | Please check top of the document - GENERAL BLOCKING SOURCES | hcw_source_element.hcw_blocking | - | - | - | - | - | - | YES
| Inlet temperature | R | Input Register | 8203 | val_d2_fp100 | Measured temperature of the inlet heating/cooling water. | hcw_source.hcw_inlet_temp | - | - | - | - | - | - | YES
| Requested temperature | R | Input Register | 8204 | val_d2_fp100 | Requested temperature for heat pump | hcw_source_element.hcws_element_request.requested_temp | - | - | - | - | - | - | YES
| Name | R/W | Holding Register | 08201-08216 | val_utf8 | String description (32 Bytes, UTF8, NULL terminated) | hcw_source_element.name | - | - | - | - | - | - | YES
| Minimum runtime [min] | R/W | Holding Register | 8217 | val_u2 | Minimum runtime in minutes | hcw_source_element.demand_minimum_time | - | - | - | - | - | - | YES
| Minimum cycle delay [min] | R/W | Holding Register | 8218 | val_u2 | Minimum cycle delay in minutes | hcw_source_element.demand_cooldown_time | - | - | - | - | - | - | YES
| Demand start delay [min] | R/W | Holding Register | 8219 | val_u2 | Demand start delay in minutes | hcw_source_element.demand_start_delay | - | - | - | - | - | - | YES
| Demand stop delay [min] | R/W | Holding Register | 8220 | val_u2 | Demand stop delay in minutes | hcw_source_element.demand_stop_delay | - | - | - | - | - | - | YES
Buffer Tank
| Aggregated warning | R | Discrete Inputs | 8301 |  | A problem is pending in Buffer Tank | - | - | - | - | - | - | - | YES
| Aggregated error | R | Discrete Inputs | 8302 |  | A critical problem is pending in Buffer Tank | - | - | - | - | - | - | - | YES
| Error - inlet temp sensor failure | R | Discrete Inputs | 8303 |  | Inlet temperature sensors failure | hcw_source.err_inlet_sensor_fail | - | - | - | - | - | - | YES
| Error - priority temp sensor failure | R | Discrete Inputs | 8304 |  | Prority temperature sensor failure | hcws_buffer_tank.err_priority_temp_unavailable | - | - | - | - | - | - | YES
| Error - upper temp sensor failure | R | Discrete Inputs | 8305 |  | Upper temperature sensor failure | hcws_buffer_tank.err_upper_temp_unavailable | - | - | - | - | - | - | YES
| Error - lower temp sensor failure | R | Discrete Inputs | 8306 |  | Lower temperature sensor failure | hcws_buffer_tank.err_lower_temp_unavailable | - | - | - | - | - | - | YES
| State | R | Input Register | 8301 | val_u1 | 1 IDLE 2 HEATING_PREPARE 3 HEATING_ACTIVE 4 HEATING_TERMINATE 5 COOLING_PREPARE 6 COOLING_ACTIVE 7 COOLING_TERMINATE 8 BLOCKED_HEATING 9 BLOCKED_COOLING 10 FAILURE | hcw_source_element.hcws_element_status hcw_source_element.hcw_blocking | - | - | - | - | - | - | YES
| Blocking source | R | Input Register | 8302 | val_u1 | Please check top of the document - GENERAL BLOCKING SOURCES | hcw_source_element.hcw_blocking | - | - | - | - | - | - | YES
| Source inlet temperature | R | Input Register | 8303 | val_d2_fp100 | Measured temperature of the source inlet heating/cooling water. | hcw_source.hcw_inlet_temp | - | - | - | - | - | - | YES
| Buffer upper temperature | R | Input Register | 8304 | val_d2_fp100 | Buffer tank upper temperature | hcws_buffer_tank.tank_upper_temp | - | - | - | - | - | - | YES
| Buffer lower temperature | R | Input Register | 8305 | val_d2_fp100 | Buffer tank lower temperature | hcws_buffer_tank.tank_lower_temp | - | - | - | - | - | - | YES
| Name | R/W | Holding Register | 08301-08316 | val_utf8 | String description (32 Bytes, UTF8, NULL terminated) | hcw_source_element.name | - | - | - | - | - | - | YES
| Start difference [K] | R/W | Holding Register | 8317 | val_d2_fp100 | Start charging difference in kelvins | hcws_buffer_tank.charge_start_temp_diff | - | - | - | - | - | - | YES
| Stop difference [K] | R/W | Holding Register | 8318 | val_d2_fp100 | Stop charging difference in kelvins | hcws_buffer_tank.charge_stop_temp_diff | - | - | - | - | - | - | YES
| Sensor priority | R/W | Holding Register | 8319 | val_u1 | 0 - UPPER_SENSOR 1 - LOWER_SENSOR | hcws_buffer_tank.charge_priority_temp_sensor | - | - | - | - | - | - | YES
| Flow balancing | R/W | Holding Register | 8320 | val_u1 | 0 - DISABLE 1 - ENABLE | hcws_buffer_tank.flow_balancing.enable | - | - | - | - | - | - | YES
| Charge mode | R/W | Holding Register | 8321 | val_u1 | 0 - CONSUMER_ONLY 1 - DEMAND_TRIGGERED | hcws_buffer_tank.charge_mode | - | - | - | - | - | - | YES
| Charge evaluation delay [min] | R/W | Holding Register | 8322 | val_u1 | Charge evaluation delay in minutes | hcws_buffer_tank.charge_evaluation_delay | - | - | - | - | - | - | YES
Reserved for another controllers |  |  |  | 100xx-127xx
HARDWARE I/O
Thermistor Inputs
| T1 - Thermistor input temp | R | Input Register | 12801 | val_d2_fp100 | T1 temperature | input.value | - | - | - | - | - | - | YES
| T2 - Thermistor input temp | R | Input Register | 12802 | val_d2_fp100 | T2 temperature | input.value | - | - | - | - | - | - | YES
| T3 - Thermistor input temp | R | Input Register | 12803 | val_d2_fp100 | T3 temperature | input.value | - | - | - | - | - | - | YES
| T4 - Thermistor input temp | R | Input Register | 12804 | val_d2_fp100 | T4 temperature | input.value | - | - | - | - | - | - | YES
| T5 - Thermistor input temp | R | Input Register | 12805 | val_d2_fp100 | T5 temperature | input.value | - | - | - | - | - | - | YES
PROGRAMABLE OUTPUTS (Logical)
PGO 1 |  |  |  | 128xx |  | NOTE: Outputs with scheduler and blockation controled from mobile application
| Name | R/W | [5 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| Value | R |  |  |  | ACTIVATED ¦ DEACTIVATED |  | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| Value Source | R |  |  |  | INPUT, SCHEDULER, USER, TEMPORARY, BMS |  | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| Blocking | R |  |  |  | NONE, STANDBY, VACATION, INPUT, SCHEDULER |  | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| Controled by BMS | R/W |  |  |  | NO ¦ YES |  | - | - | - |  |  |  |  | BLOCKED .. needs architecture
PGO 2 |  |  |  | 129xx
PGO 3 |  |  |  | 130xx
… |  |  |  | …
PGO 8 |  |  |  | 135xx
Reserved | For PGO9 - PGO32 |  |  | 136xx-159xx
PROGRAMABLE INPUTS (Logical)
PGI 1 |  |  |  | 160xx
| Name | R/W | [5 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| Value | R/W | [5 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
PGI 2 |  |  |  | 161xx
PGI 3 |  |  |  | 162xx
… |  |  |  | …
PGI 8 |  |  |  | 167xx
Reserved | For PGI9 - PGI32 |  |  | 168xx-191xx
HARDWARE I/O (physical)
CCU-208 |  |  |  | 256xx
| O1 GPIO | [6 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| O1 name | R/W | [5 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| O1 output - status | R/W | [5 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| O1 function Input / Output - status | R/W | [5 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| O1 output - taking over ccontrol | R/W | [5 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
[8 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| O2 GPIO | [6 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| O2 output - status | R/W | [5 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| O2 function Input / Output - status | R/W | [5 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| O2 output - taking over ccontrol | R/W | [5 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
[8 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| Analog output | [6 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| AO - Analog output status | R/W | [5 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| AO - Analog output - taking over control | R/W | [5 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
[8 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| PO Pulse output | [6 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| PO output status | R/W | [5 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| PO output - takoing over | R/W | [5 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
[8 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| Pumps | [6 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| P1 - P2 value | R/W | [5 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| P1 - P2 taking over control | R/W | [5 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
[8 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| Outputs for TH | [6 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| A1 - A8 Value | R/W | [5 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| A1 - A8 taking over control | R/W | [5 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
[8 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| Relay outputs | [6 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| VFR1 - VFR32 Value | R/W | [5 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| VFR1 - VFR32 takig over | R/W | [5 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
[8 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| Thermometer inputs | [6 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| T1 - T5 | R | [5 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
[8 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| O1 GPIO | [6 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| O1 input - value | R |  |  |  | break the influence from physic inut |  | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| O1 input - taking over control | R/W |  |  |  | input a value for next processes |  | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| O1 value | R/W | [5 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
[6 empty] | physical input value read from input |  | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| O2 GPIO | [6 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| O2 input - value | R |  |  |  | break the influence from physic inut |  | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| O2 input - taking over control | R/W |  |  |  | input a value for next processes |  | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| O2 value | R/W | [5 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
[6 empty] | physical input value read from input |  | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| Pulse input | [6 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| PI input - value | R |  |  |  | break the influence from physic inut |  | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| PI input - taking over control | R/W |  |  |  | input a value for next processes |  | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| PI value | [6 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
EU-208-A [1] |  |  |  | 25700 |  | NOTE: The expander modbus slot ([1], [2], [3], [4]) is fixed and defined by learn order. It will be possible to change the slot using LCD |  | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| Name | R/W |  | 25701-25731 |  | Expander name |  | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| SN | R |  | 25732 |  | Expander serial number |  | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| reserved | - | [5 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| Outputs for TH | [6 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| A09 Value | R/W | [5 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| A10 Value | R/W | [5 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| A11 Value | R/W | [5 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| … | … | [5 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| A16 Value | R/W | [5 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
[8 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| A09 Controled by BMS | R/W | [5 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| A10 Controled by BMS | R/W | [5 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| A11 Controled by BMS | R/W | [5 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| … | [6 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| A16 Controled by BMS | R/W | [5 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
[8 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
EU-208-A [2] | same as EU-208-A [1] |  |  | 25800 |  |  |  | - | - | - |  |  |  |  | BLOCKED .. needs architecture
EU-208-A [3] | same as EU-208-A [1] |  |  | 25900 |  |  |  | - | - | - |  |  |  |  | BLOCKED .. needs architecture
EU-208-A [4] | same as EU-208-A [1] |  |  | 26000 |  |  |  | - | - | - |  |  |  |  | BLOCKED .. needs architecture
[8 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
EU-206-VFR[1] |  |  |  | 26100 |  | NOTE: The expander modbus slot ([1], [2], [3], [4], [5], [6]) fixed and defined by learn order. It will be possible to change the slot using LCD |  | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| Name | R/W |  | 26101 |  |  |  | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| SN | R |  | 26102 |  |  |  | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| reserved | - |  | 26103 |  |  |  | - | - | - |  |  |  |  | BLOCKED .. needs architecture
[8 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| VFR-A Value | R |  | 26111 |  |  |  | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| VFR-B Value | R |  | 26112 |  |  |  | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| … | … | [5 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| VFR-F Value | R |  | 26116 |  |  |  | - | - | - |  |  |  |  | BLOCKED .. needs architecture
[8 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| VFR-A Controled by Modbus | R/W |  | 26117 |  |  |  | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| VFR-B Controled by Modbus | R/W |  | 26118 |  |  |  | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| … | …. | [5 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
| VFR-F Controled by Modbus | R/W | [5 empty] | - | - | - |  |  |  |  | BLOCKED .. needs architecture
EU-206-VFR[2] |  |  |  | 26200 |  |  |  | - | - | - |  |  |  |  | BLOCKED .. needs architecture
EU-206-VFR[3] |  |  |  | 26300 |  |  |  | - | - | - |  |  |  |  | BLOCKED .. needs architecture
EU-206-VFR[4] |  |  |  | 26400 |  |  |  | - | - | - |  |  |  |  | BLOCKED .. needs architecture
EU-206-VFR[5] |  |  |  | 26500 |  |  |  | - | - | - |  |  |  |  | BLOCKED .. needs architecture
EU-206-VFR[6] |  |  |  | 26600 |  |  |  | - | - | - |  |  |  |  | BLOCKED .. needs architecture
PERIPHERAL LIST
Peripheral 1 |  |  |  | 512xx |  | NOTE: Dynamic list of peripherals. Position of the peripherals is not fixed. It can change when a peripheral is learned or unlearned.
| Aggregated warning | R | Discrete Inputs | 51201 |  | A problem is pending in Room | - | - | - | YES | YES | YES | YES | YES
| Aggregated error | R | Discrete Inputs | 51202 |  | A critical problem is pending in Room | - | - | - | YES | YES | YES | YES | YES
| Warning - low battery | R | Discrete Inputs | 51203 |  | Battery is low in the peripheral. | device.warn_low_batery | - | - | YES | YES | YES | YES | YES
| Error - peripheral lost | R | Discrete Inputs | 51204 |  | Peripheral is not responding. | device.warn_unreachable | - | - | YES | YES | YES | YES | YES
| Type | R | Input Register | 51201 | val_u2 | Peripheral type - Sensor, Termostat, see table at the top | GetProductType(device.sn) | - | - | YES | YES | YES | YES | YES
| SN | R | Input Register | 51202-51203 | val_u4 | Serial number | device.sn | - | - | YES | YES | YES | YES | YES
| Owner | R | Input Register | 51204 | val_u2 | 000 - Location 001 - Room 1 … 016 - Room 16 NOTE: Object address in this modbus table is used as owner_id | GetModbusAddress(device.owner_id) | - | - | YES | YES | YES | YES | YES
| Signal strength | R | Input Register | 51205 | val_u1 | Peripheral Signal strength 0 - 6, 0 - worst signal … 6 - best signal | Min(device.signal_strength_tx, device.signal_strength_rx) | - | - | YES | CHANGED | YES | YES | YES
| Peripheral name | R/W | Holding register | 51201 - 51216 | val_utf8 | String description (32 Bytes, UTF8, NULL terminated) | device.name | - | - | YES | YES | YES | YES | YES
Peripheral 2 |  |  |  | 513xx
Peripheral 3 |  |  |  | 514xx
….
Peripheral 2-64 |  |  |  | 575xx
Reserved | For peripherals 64-128 |  |  | 576x-640xx
EXTERNAL DEVICES
Ventilation 1 |  |  |  | 610xx
| Aggregated warning | R | Discrete Inputs | 61001 |  | A problem is pending in device | - | - | - | - | - | - | YES | YES
| Aggregated error | R | Discrete Inputs | 61002 |  | A critical problem is pending in device | - | - | - | - | - | - | YES | YES
| Warning - air filter lifetime expired | R | Discrete Inputs | 61003 |  | Air filter lifetime expired | edevMVDI.warn_air_filter_replace = 1 | - | - | - | - | - | YES | YES
| Warning - air filter solar year passed | R | Discrete Inputs | 61004 |  | Air filter solar year passed from last air filter change | edevMVDI.warn_air_filter_replace = 2 | - | - | - | - | - | YES | YES
| Warning - device specific | R | Discrete Inputs | 61005 |  | Read code from input register - Warning-device specific | edevMVDI.device_specific_warning | - | - | - | - | - | YES | YES
| Error - device fault | R | Discrete Inputs | 61006 |  | General problem | edevMVDI.err_device_fault = 1 | - | - | - | - | - | YES | YES
| Error - communication error | R | Discrete Inputs | 61007 |  | Communication error | edevMVDI.err_device_fault = 2 | - | - | - | - | - | YES | YES
| Error - not compatible | R | Discrete Inputs | 61008 |  | Not compatible | edevMVDI.err_device_fault = 3 | - | - | - | - | - | YES | YES
| Error - device specific | R | Discrete Inputs | 61009 |  | Read code from input register - Error-device specific | edevMVDI.device_specific_error | - | - | - | - | - | YES | YES
| Device model | R | Input Register | 61001-61016 | val_utf8 | Device model | edevMVDI.MV.device_model | - | - | - | - | - | YES | YES
| Warning - device specific code | R | Input Register | 61017-61018 | val_u4 | Device specific warning code | edevMVDI.device_specific_warning | - | - | - | - | - | YES | YES
| Error - device specific code | R | Input Register | 61019-61020 | val_u4 | Device specific error code | edevMVDI.device_specific_error | - | - | - | - | - | YES | YES
| Device feature bits | R | Input Register | 61021-61022 | val_u4 | Specific features (capabilities) device has 0x0001 - ALLOW_UNOCCUPIED 0x0002 - ALLOW_ECO 0x0004 - ALLOW_COMFORT 0x0008 - ALLOW_STOPPED 0x0010 - ALLOW_BOOST 0x0020 - ALLOW_BYPASS 0x0040 - FAN_PWM_CONTROL 0x0080 - FAN_BINARY_CONTROL 0x0100 - TEMP_INTAKE 0x0200 - TEMP_SUPPLY 0x0400 - TEMP_EXTRACT 0x0800 - TEMP_EXHAUST 0x1000 - HUMIDITY_INTAKE 0x2000 - HUMIDITY_EXTRACT 0x4000 - FAN_SPEED_FEEDBACK | edevMVDI.MV.device_features | - | - | - | - | - | YES | YES
| Ventilation state | R | Input Register | 61023 | val_u1 | 0 - STOPPED 1 - UNOCCUPIED 2 - ECONOMY 3 - COMFORT 4 - BOOST 5 - BLOCKED_STOPPED 6 - BLOCKED_UNOCCUPIED 7 - BLOCKED_ECONOMY 8 - BLOCKED_COMFORT 9 - BLOCKED_BOOST 10 - FAILURE 11 - MAINTENANCE | common.ventilation.ventlation_src_status.actual_level common.ventilation.ventlation_src_status.blocking | - | - | - | - | - | YES | YES
| Ventilation blocking | R | Input Register | 61024 | val_u1 | Please check top of the document - GENERAL BLOCKING SOURCES | common.ventilation.ventlation_src_status.blocking | - | - | - | - | - | YES | YES
Feature bit - FAN_SPEED_FEEDBACK | Supply fan speed actual [rpm] | R | Input Register | 61025 | val_u2 | Supply fan speed actual [rpm] | edevMVDI.MV.fan_speed_supply_rpm | - | - | - | - | - | YES | YES
Feature bit - FAN_SPEED_FEEDBACK | Exhaust fan speed actual [rpm] | R | Input Register | 61026 | val_u2 | Exhaust fan speed actual [rpm] | edevMVDI.MV.fan_speed_exhaust_rpm | - | - | - | - | - | YES | YES
Feature bit - FAN_PWM_CONTROL | Supply fan speed setpoint [%] | R | Input Register | 61027 | val_d2_fp100 | Supply fan speed setpoint [%] | edevMVDI.MV.fan_speed_supply | - | - | - | - | - | YES | YES
Feature bit - FAN_PWM_CONTROL | Exhaust fan speed setpoint [%] | R | Input Register | 61028 | val_d2_fp100 | Exhaust fan speed setpoint [%] | edevMVDI.MV.fan_speed_exhaust | - | - | - | - | - | YES | YES
Feature bit - !FAN_PWM_CONTROL | Supply volume flow setpoint [m^3/h] | R | Input Register | 61029 | val_u2 | Supply volume flow setpoint [m^3/h] | edevMVDI.MV.supply_volume_flow | - | - | - | - | - | YES | YES
Feature bit - !FAN_PWM_CONTROL | Exhaust volume flow setpoint [m^3/h] | R | Input Register | 61030 | val_u2 | Exhaust volume flow setpoint [m^3/h] | edevMVDI.MV.exhaust_volume_flow | - | - | - | - | - | YES | YES
Feature bit - TEMP_INTAKE | Intake air temperature | R | Input Register | 61031 | val_d2_fp100 | Intake air temperature | edevMVDI.MV.temp_intake | - | - | - | - | - | YES | YES
Feature bit - TEMP_SUPPLY | Supply air temperature | R | Input Register | 61032 | val_d2_fp100 | Supply air temperature | edevMVDI.MV.temp_supply | - | - | - | - | - | YES | YES
Feature bit - TEMP_EXTRACT | Extract air temperature | R | Input Register | 61033 | val_d2_fp100 | Extract air temperature | edevMVDI.MV.temp_extract | - | - | - | - | - | YES | YES
Feature bit - TEMP_EXHAUST | Exhaust air temperature | R | Input Register | 61034 | val_d2_fp100 | Exhaust air temperature | edevMVDI.MV.temp_exhaust | - | - | - | - | - | YES | YES
Feature bit - ALLOW_BYPASS | Heat recovery bypass damper position [%] | R | Input Register | 61035 | val_d2_fp100 | Heat recovery bypass damper position [%] | edevMVDI.MV.bypass_damper_position | - | - | - | - | - | YES | YES
Feature bit - ALLOW_BYPASS | Free cooling enabled | R | Input Register | 61036 | val_u1 | Free cooling enabled | edevMVDI.MV.free_cooling_enabled | - | - | - | - | - | YES | YES
| Air filter last change | R | Input Register | 61037-61038 | val_u4 | Timestamp, updates when register "Air filter lifetime used" is set to zero | edevMVDI.air_filter_last_change | - | - | - | - | - | YES | YES
| Device name | R/W | Holding register | 61001-61016 | val_utf8 | String description (32 Bytes, UTF8, NULL terminated) | device.name | - | - | - | - | - | YES | YES
| Air filter lifetime | R/W | Holding Register | 61017-61018 | val_u4 | Air filter lifetime (minutes) - maximum value is dependent on device model | edevMVDI.air_filter_lifetime | - | - | - | - | - | YES | YES
| Air filter lifetime used | R/W | Holding Register | 61019-61020 | val_u4 | Write 0 to reset timer | edevMVDI.air_filter_lifetime_used | - | - | - | - | - | YES | YES
Feature bit - FAN_PWM_CONTROL | Exhaust Fan Level Unoccupied [%] | R/W | Holding register | 61021 | val_d2_fp100 | Exhaust Fan Level Unoccupied [%] | edevMVDI.MV.exhaust_fan_level_unoccupied_percent | - | - | - | - | - | YES | YES
Feature bit - FAN_PWM_CONTROL | Exhaust Fan Level Eco [%] | R/W | Holding register | 61022 | val_d2_fp100 | Exhaust Fan Level Eco [%] | edevMVDI.MV.exhaust_fan_level_eco_percent | - | - | - | - | - | YES | YES
Feature bit - FAN_PWM_CONTROL | Exhaust Fan Level Comfort [%] | R/W | Holding register | 61023 | val_d2_fp100 | Exhaust Fan Level Comfort [%] | edevMVDI.MV.exhaust_fan_level_comfort_percent | - | - | - | - | - | YES | YES
Feature bit - FAN_PWM_CONTROL | Exhaust Fan Level Boost [%] | R/W | Holding register | 61024 | val_d2_fp100 | Exhaust Fan Level Boost [%] | edevMVDI.MV.exhaust_fan_level_boost_percent | - | - | - | - | - | YES | YES
Feature bit - FAN_PWM_CONTROL | Supply Fan Level Unoccupied [%] | R/W | Holding register | 61025 | val_d2_fp100 | Supply Fan Level Unoccupied [%] | edevMVDI.MV.supply_fan_level_unoccupied_percent | - | - | - | - | - | YES | YES
Feature bit - FAN_PWM_CONTROL | Supply Fan Level Eco [%] | R/W | Holding register | 61026 | val_d2_fp100 | Supply Fan Level Eco [%] | edevMVDI.MV.supply_fan_level_eco_percent | - | - | - | - | - | YES | YES
Feature bit - FAN_PWM_CONTROL | Supply Fan Level Comfort [%] | R/W | Holding register | 61027 | val_d2_fp100 | Supply Fan Level Comfort [%] | edevMVDI.MV.supply_fan_level_comfort_percent | - | - | - | - | - | YES | YES
Feature bit - FAN_PWM_CONTROL | Supply Fan Level Boost [%] | R/W | Holding register | 61028 | val_d2_fp100 | Supply Fan Level Boost [%] | edevMVDI.MV.supply_fan_level_boost_percent | - | - | - | - | - | YES | YES
Feature bit - !FAN_PWM_CONTROL | Exhaust Fan Level Unoccupied [m^3/h] | R/W | Holding register | 61029 | val_u2 | Exhaust Fan Level Unoccupied [m^3/h] | edevMVDI.MV.exhaust_fan_level_unoccupied_vol | - | - | - | - | - | YES | YES
Feature bit - !FAN_PWM_CONTROL | Exhaust Fan Level Eco [m^3/h] | R/W | Holding register | 61030 | val_u2 | Exhaust Fan Level Eco [m^3/h] | edevMVDI.MV.exhaust_fan_level_eco_vol | - | - | - | - | - | YES | YES
Feature bit - !FAN_PWM_CONTROL | Exhaust Fan Level Comfort [m^3/h] | R/W | Holding register | 61031 | val_u2 | Exhaust Fan Level Comfort [m^3/h] | edevMVDI.MV.exhaust_fan_level_comfort_vol | - | - | - | - | - | YES | YES
Feature bit - !FAN_PWM_CONTROL | Exhaust Fan Level Boost [m^3/h] | R/W | Holding register | 61032 | val_u2 | Exhaust Fan Level Boost [m^3/h] | edevMVDI.MV.exhaust_fan_level_boost_vol | - | - | - | - | - | YES | YES
Feature bit - !FAN_PWM_CONTROL | Exhaust Fan Level Boost [m^3/h] | R/W | Holding register | 61033 | val_u2 | Supply Fan Level Unoccupied [m^3/h] | edevMVDI.MV.supply_fan_level_unoccupied_vol | - | - | - | - | - | YES | YES
Feature bit - !FAN_PWM_CONTROL | Supply Fan Level Eco [m^3/h] | R/W | Holding register | 61034 | val_u2 | Supply Fan Level Eco [m^3/h] | edevMVDI.MV.supply_fan_level_eco_vol | - | - | - | - | - | YES | YES
Feature bit - !FAN_PWM_CONTROL | Supply Fan Level Comfort [m^3/h] | R/W | Holding register | 61035 | val_u2 | Supply Fan Level Comfort [m^3/h] | edevMVDI.MV.supply_fan_level_comfort_vol | - | - | - | - | - | YES | YES
Feature bit - !FAN_PWM_CONTROL | Supply Fan Level Boost [m^3/h] | R/W | Holding register | 61036 | val_u2 | Supply Fan Level Boost [m^3/h] | edevMVDI.MV.supply_fan_level_boost_vol | - | - | - | - | - | YES | YES
Feature bit - ALLOW_STOPPED | Allow Stopped level | R/W | Holding register | 61037 | val_u1 | Allow Stopped level 0 - NOT ALLOWED 1 - ALLOWED | edevMVDI.MV.allow_stopped_level | - | - | - | - | - | YES | YES
Feature bit - ALLOW_UNOCCUPIED | Allow Unoccupied level | R/W | Holding register | 61038 | val_u1 | Allow Unoccupied level 0 - NOT ALLOWED 1 - ALLOWED | edevMVDI.MV.allow_unoccupied_level | - | - | - | - | - | YES | YES
Depends on "Allow Stopped level", "Allow Unoccupied Level" and feature bits | Standby mode level | R/W | Holding register | 61039 | val_u1 | 0 - STOPPED 1 - UNOCCUPIED 2 - ECONOMY | edevMVDI.MV.standby_level | - | - | - | - | - | YES | YES
Depends on "Allow Stopped level", "Allow Unoccupied Level" and feature bits | Vacation mode level | R/W | Holding register | 61040 | val_u1 | 0 - STOPPED 1 - UNOCCUPIED 2 - ECONOMY | edevMVDI.MV.vacation_level | - | - | - | - | - | YES | YES
Feature bit - ALLOW_BYPASS | Heat exchange mode (recovery bypass) | R/W | Holding register | 61041 | val_u1 | 0 - ALWAYS ON 1 - AUTOMATIC | edevMVDI.MV.bypass_mode | - | - | - | - | - | YES | YES
Ventilation 2 |  |  |  | 611xx |  |  |  | - | - | - | - | - | YES | YES
reserved | For Ventilation 3-4 |  |  | 612xx-613xx |  |  |  | - | - | - | - | -
[8 empty] | - | - | - | - | -
Dehumidifier 1 |  |  |  | 650xx
| Aggregated warning | R | Discrete Inputs | 65001 |  | A problem is pending in device | - | - | - | - | YES | YES | YES | YES
| Aggregated error | R | Discrete Inputs | 65002 |  | A critical problem is pending in device | - | - | - | - | YES | YES | YES | YES
| Warning - air filter lifetime expired | R | Discrete Inputs | 65003 |  | Air filter lifetime expired | edevMVDI.warn_air_filter_replace = 1 | - | - | - | YES | YES | YES | YES
| Warning - air filter solar year passed | R | Discrete Inputs | 65004 |  | Air filter solar year passed from last air filter change | edevMVDI.warn_air_filter_replace = 2 | - | - | - | YES | YES | YES | YES
| Error - HCW supplier | R | Discrete Inputs | 65005 |  | Heating/Cooling water supplier is not set | edevMVDI.err_no_hcw_supplier | - | - | - | YES | YES | YES | YES
| Error - device fault | R | Discrete Inputs | 65006 |  | Device fault - general signal from device | edevMVDI.err_device_fault | - | - | - | YES | YES | YES | YES
| Type | R | Input Register | 65001 | val_u1 | Device type 0 GENERIC 1 P300_S300 2 PC300_SC300 | edevMVDI.type | - | - | - | YES | YES | YES | YES
| Subtype - reserved | R | Input Register | 65002 | reserved | reserved |  | - | - | - | - | - | - | -
| Drying status | R | Input Register | 65003 | val_u1 | 0 NONE (function not available) 1 IDLE 2 DRYING 3 BLOCKED_DRYING | edevMVDI.drying_state | - | - | - | YES | YES | YES | YES
| Drying blocking | R | Input Register | 65004 | val_u1 | Please check top of the document - GENERAL BLOCKING SOURCES | edevMVDI.drying_blocking | - | - | - | YES | YES | YES | YES
| Thermal integration status | R | Input Register | 65005 | val_u1 | 0 NONE (function not available) 1 IDLE 2 HEATING 3 COOLING 4 BLOCKED_HEATING 5 BLOCKED_COOLING | edevMVDI.integration_state | - | - | - | YES | YES | YES | YES
| Thermal integration blocking | R | Input Register | 65006 | val_u1 | Please check top of the document - GENERAL BLOCKING SOURCES | edevMVDI.integration_blocking | - | - | - | YES | YES | YES | YES
| Thermal Integ. demand condition | R | Input Register | 65007 | val_u1 | 100 - IN ANY ROOM 101 - IN ALL ROOMS 1-32 - PARTICULAR ROOM (Address of modbus object) | edevMVDI.integAggregator.demand_condition | - | - | - | YES | YES | YES | YES
| Ventilation status | R | Input Register | 65008 | val_u1 | 0 NONE (function not available) 1 IDLE 2 VENTILATING 3 BLOCKED_VENTILATING | edevMVDI.ventilation_state | - | - | - | - | - | - | -
| Ventilation blocking | R | Input Register | 65009 | val_u1 | Please check top of the document - GENERAL BLOCKING SOURCES | edevMVDI.ventilation_blocking | - | - | - | - | - | - | -
| Air filter last change | R | Input Register | 65010-11 | val_u4 | Timestamp, updates when register "Air filter lifetime used" is set to zero | edevMVDI.air_filter_last_change | - | - | - | YES | YES | YES | YES
| Associated HCW supplier | R | Input Register | 65012 | val_u1 | 0 .. NONE 73 .. ITC1 (Address of modbus object) 74 .. ITC2 (Address of modbus object) 77 .. HCC1 (Address of modbus object) 78 .. HCC2 (Address of modbus object) 79 .. HCC3 (Address of modbus object) 81 .. H/C Source (Address of modbus object) | edevMVDI.hcw_supplier_oid | - | - | - | YES | YES | YES | YES
| Device name | R/W | Holding register | 65001-65016 | val_utf8 | String description (32 Bytes, UTF8, NULL terminated) | device.name | - | - | - | YES | YES | YES | YES
| Air filter lifetime | R/W | Holding Register | 65017-65018 | val_u4 | Air filter lifetime (minutes) | edevMVDI.air_filter_lifetime | - | - | - | YES | YES | YES | YES
| Air filter lifetime used | R/W | Holding Register | 65019-65020 | val_u4 | Write 0 to reset timer | edevMVDI.air_filter_lifetime_used | - | - | - | YES | YES | YES | YES
| Drying allow in mode | R/W | Holding Register | 65021 | val_u1 | 0 - IN COOLING MODE 1 - IN HEATING MODE 2 - IN BOTH | edevMVDI.dryingAggregator.allow_mode | - | - | - | YES | YES | YES | YES
| Drying cooling water | R/W | Holding Register | 65022 | val_d2_fp100 | Desired cooling water temperature | edevMVDI.drying_required_cooling_water_temp | - | - | - | YES | YES | YES | YES
| Thermal integ. allow in mode | R/W | Holding Register | 65023 | val_u1 | 0 - IN COOLING MODE 1 - IN HEATING MODE 2 - IN BOTH | edevMVDI.integAggregator.allow_mode | - | - | - | YES | YES | YES | YES
| Thermal integ. heating water temp | R/W | Holding Register | 65024 | val_d2_fp100 | Desired heating water temperature | edevMVDI.integration_required_heating_water_temp | - | - | - | YES | YES | YES | YES
| Thermal integ. cooling water temp | R/W | Holding Register | 65025 | val_d2_fp100 | Desired cooling water temperature | edevMVDI.integration_required_cooling_water_temp | - | - | - | YES | YES | YES | YES
Dehumidifier 2 |  |  |  | 651xx |  |  |  | - | - | - | YES | YES | YES | YES
Dehumidifier 3 |  |  |  | 652xx |  |  |  | - | - | - | YES | YES | YES | YES
Dehumidifier 4 |  |  |  | 653xx |  |  |  | - | - | - | YES | YES | YES | YES
Note on L30: Šindelář Jiří: Added 3 WRITE_WITH_PASSWORD
Note on H54: Šindelář Jiří: When “Room mode override” > NONE, then this temperature is defined by override mode. When “Room mode” == SCHEDULE, then this temperature is defined by room schedule. When (“Room mode” == MANUAL) AND (“Room mode override” == NONE) then this temperature is defined by “Room temperature setpoint”
Note on L55: Šindelář Jiří: Added: 4 BLOCKED_HEATING 5 BLOCKED_COOLING
Note on L56: Šindelář Jiří: Added: 10 PERIODIC_ACTIVATION
Note on C435: VFR should be renamed to "Output" because VFR is type of output only

## Timezone list
List of supported IANA timezones
Area/Town | UTC offset | Zone number
Factory |  | 0
Europe/Amsterdam | +01:00 | 1024
Europe/Astrakhan | +04:00 | 1025
Europe/Berlin | +01:00 | 1026
Europe/Bratislava | +01:00 | 1027
Europe/Brussels | +01:00 | 1028
Europe/Budapest | +01:00 | 1029
Europe/Copenhagen | +01:00 | 1030
Europe/Dublin | +00:00 | 1031
Europe/Helsinki | +02:00 | 1032
Europe/Istanbul | +03:00 | 1033
Europe/Kaliningrad | +02:00 | 1034
Europe/Kirov | +03:00 | 1035
Europe/London | +00:00 | 1036
Europe/Madrid | +01:00 | 1037
Europe/Moscow | +03:00 | 1038
Europe/Oslo | +01:00 | 1039
Europe/Paris | +01:00 | 1040
Europe/Prague | +01:00 | 1041
Europe/Riga | +02:00 | 1042
Europe/Rome | +01:00 | 1043
Europe/Samara | +04:00 | 1044
Europe/Saratov | +04:00 | 1045
Europe/Stockholm | +01:00 | 1046
Europe/Ulyanovsk | +04:00 | 1047
Europe/Vilnius | +02:00 | 1048
Europe/Volgograd | +03:00 | 1049
Europe/Warsaw | +01:00 | 1050
Atlantic/Faroe | +00:00 | 2048
Atlantic/Reykjavik | +00:00 | 2049
America/Cancun | -05:00 | 3072
America/Chihuahua | -07:00 | 3073
America/Danmarkshavn | +00:00 | 3074
America/Godthab | -03:00 | 3075
America/Hermosillo | -07:00 | 3076
America/Matamoros | -06:00 | 3077
America/Mexico_City | -06:00 | 3078
America/Ojinaga | -07:00 | 3079
America/Scoresbysund | -01:00 | 3080
America/Thule | -04:00 | 3081
America/Tijuana | -08:00 | 3082
Asia/Anadyr | +12:00 | 4096
Asia/Barnaul | +07:00 | 4097
Asia/Chita | +09:00 | 4098
Asia/Irkutsk | +08:00 | 4099
Asia/Kamchatka | +12:00 | 4100
Asia/Khandyga | +09:00 | 4101
Asia/Krasnoyarsk | +07:00 | 4102
Asia/Magadan | +11:00 | 4103
Asia/Novokuznetsk | +07:00 | 4104
Asia/Novosibirsk | +07:00 | 4105
Asia/Omsk | +06:00 | 4106
Asia/Sakhalin | +11:00 | 4107
Asia/Srednekolymsk | +11:00 | 4108
Asia/Tomsk | +07:00 | 4109
Asia/Ust-Nera | +10:00 | 4110
Asia/Vladivostok | +10:00 | 4111
Asia/Yakutsk | +09:00 | 4112
Asia/Yekaterinburg | +05:00 | 4113
Factory timezone Factory timezone is read-only. It is used for compatibility reasons. E.g. When updating from SW which didnt support timezones.
UTC offset is last known, DST rules are same as for Europe.
When Factory is set, you should change it to supported timezone.

## regMap
Verze: | 3.1
Adresa: | 1
|  | type | start addr | register name | var_type | access | mul | min | max | default | units | register vid | iteration count | mb_offset | variable_offset | description EN
Location |  | IDR | 1 | location_aggregated_warning | bool |  | 1
|  | IDR | 1 | location_aggregated_error | bool |  | 1
|  | IR | 1 | location_address_space_major_version | val_u1 |  | 1 | [8 empty] | 3 - incremented on incompatible change
|  | IR | 2 | location_address_space_minor_version | val_u1 |  | 1 | [8 empty] | 1 - Incremented on compatible change
|  | IR | 10 | location_dev_type | val_u1 |  | 1 | 0
|  | IR | 11 | location_dev_hw_version | val_u1 |  | 1 |  |  |  |  | device.hw_version
|  | IR | 12 | location_dev_sw_version | val_u1 |  | 1 |  |  |  |  | device.sw_version
|  | IR | 13 | location_dev_sw_version_minor | val_u1 |  | 1 |  |  |  |  | device.sw_version_minor
|  | IR | 14 | location_dev_serial_number_prefix | val_u2 |  | 1 |  |  |  |  | device.serial_prefix |  |  |  | 1530
|  | IR | 15 | location_dev_serial_number | val_u4 |  | 1 |  |  |  |  | device.serial
|  | IR | 20 | location_hc_mode | val_u1 |  | 1 | 0 | 1 |  |  | location.hc_mode |  |  |  | 0 – HEATING;1 – COOLING
|  | HR | 1 | location_address_space_major_version | val_u1 |  | 1
|  | HR | 2 | location_address_space_minor_version | val_u1 |  | 1
|  | HR | 3 | location_modbus_slave_address | val_u1 |  | 1 | 1 | 247 |  |  | location.modbus_addr
|  | HR | 4 | location_modbus_baudrate | val_u2 |  | 1 | 9600 | 19200 |  |  | location.modbus_baudrate
|  | HR | 5 | location_modbus_mode | val_u1 |  | 1 | 0 | 3 | 0 |  | location.modbus_mode
|  | HR | 6 | location_modbus_password | val_u2 |  | 1
|  | HR | 7 | location_modbus_parity | val_u1 |  | 1 | 0 | 2 |  |  | location.modbus_parity
|  | HR | 8 | location_modbus_stop_bits | val_u1 |  | 1 | 0 | 2 |  |  | location.modbus_stop_bits
|  | HR | 10 | location_location_name | val_utf8 |  | 1 |  |  |  |  | location.name |  |  |  | Placeholder for 32 bytes of location description.;See “working with strings” chapter for more info.
|  | HR | 26 | location_standby | val_u1 |  | 1 | 0 | 1 |  |  | location.standby |  |  |  | 0 – OFF;1 - ON
|  | HR | 27 | location_vacation | val_u1 |  | 1 | 0 | 1 |  |  | location.vacation |  |  |  | 0 – OFF;1 – ON
|  | HR | 28 | location_datetime | val_u4 |  | 1 | [8 empty] | Current time; unit timestamp format; localtime including DST (if enabled)
|  | HR | 30 | location_daylight_saving_time_allowed | val_u1 |  | 1 | 0 | 1 |  |  | location.vacation |  |  |  | 0 – Disabled;1 - Enabled
|  | HR | 31 | location_cooling_min_outdoor_temp | val_d2_fp100 |  | 1 | 1000 | 4000 | [6 empty] | Cooling is blocked, when outdoor temperature is lower than this value.
|  | HR | 32 | location_heating_max_outdoor_temp | val_d2_fp100 |  | 1 | 1000 | 4000 | [6 empty] | Heating is blocked, when outdoor temperature is higher than this value.
|  | HR | 33 | location_update_mode | val_u1 |  | 1 | 0 | 2 |  |  | update_ctrl.update_mode |  |  |  | 0 – Dont allow from mobile app;1 - Enabled;2 - Disabled entirely
|  | HR | 34 | location_hc_mode_override | val_u1 |  | 1 | 0 | 3 |  |  | location.hc_mode_priority;location.hc_mode_bms_override;location.hc_mode_hw_source |  |  |  | 0 - DISABLED;1 - HEATING MODE;2 - COOLING MODE;3 - H/C MODE SET BY EXTERNAL SWITCH (only when HW input is available)
|  | HR | 35 | location_timezone_number | val_u2 |  | 1 | [8 empty] | See tab "Timezone list" for supported timezones
Room |  | IDR | 101 | roomX_aggregated_warning | bool |  | 1 | [5 empty] | 24 | 100 | roomX | A problem is pending in Room
|  | IDR | 102 | roomX_aggregated_error | bool |  | 1 | [5 empty] | 24 | 100 | roomX | A critical problem is pending in Room
|  | IDR | 103 | roomX_low_battery_warning | bool |  | 1 |  |  |  |  | room.warn_periph_low_batery | 24 | 100 | roomX | There are one or more peripherals in the room with low battery.
|  | IDR | 104 | roomX_peripheral_lost_error | bool |  | 1 |  |  |  |  | room.alarm_periph_unreachable | 24 | 100 | roomX | There are one or more peripherals in the room which are not responding.
|  | IR | 101 | roomX_desired_temp | val_d2_fp100 |  | 1 |  |  |  |  | room.tmp_ctrl.temp_desired | 24 | 100 | roomX | Shows the desired temperature in the room.; When “Room mode override” > NONE, then this temperature is defined by override mode.;When “Room mode” == SCHEDULE, then this temperature is defined by room schedule.;When (“Room mode” == MANUAL) AND (“Room mode override” == NONE);then this temperature is defined by “Room temperature setpoint”
|  | IR | 102 | roomX_general_hc_state | val_u1 |  | 1 | 1 | 3 |  |  | room.tmp_ctrl.state;room.tmp_ctrl.blocking | 24 | 100 | roomX | 1 – IDLE;2 - HEATING;3 - COOLING;4 - BLOCKED_HEATING;5 - BLOCKED_COOLING
|  | IR | 103 | roomX_general_hc_blocking_source | val_u1 |  | 1 |  |  |  |  | room.tmp_ctrl.blocking | 24 | 100 | roomX | Please check top of the document - GENERAL BLOCKING SOURCES
|  | IR | 104 | roomX_air_temp | val_d2_fp100 |  | 1 |  |  |  |  | room.air_temp | 24 | 100 | roomX | Current air temperature measured in the room.
|  | IR | 105 | roomX_floor_temp | val_d2_fp100 |  | 1 |  |  |  |  | room.floor_temp | 24 | 100 | roomX | Current floor temperature measured in the room.
|  | IR | 106 | roomX_relative_humidity | val_d2_fp100 |  | 1 |  |  |  |  | room.humidity | 24 | 100 | roomX | Current humidity measured in the room.
|  | IR | 107 | roomX_calculated_dew_point | val_d2_fp100 |  | 1 |  |  |  |  | room.dew_point | 24 | 100 | roomX | Current calculated dewpoint
|  | IR | 111 | roomX_associated_to_radiators | val_u1 |  | 1 | 0 | 81 |  |  | room.air_hcw_ctrl.supplier_oid | 24 | 100 | roomX | 0 - NONE;73 - ITC1 (Address of modbus object);74 - ITC2 (Address of modbus object);77 - hccX (Address of modbus object);78 - HCC2 (Address of modbus object);79 - HCC3 (Address of modbus object);81 - H/C Source (Address of modbus object)
|  | IR | 112 | roomX_associated_to_ufhc | val_u1 |  | 1 | 0 | 79 |  |  | room.ufhc_hcw_ctrl.hcw_supplier_oid | 24 | 100 | roomX | 0 - NONE;73 - ITC1 (Address of modbus object);74 - ITC2 (Address of modbus object);77 - hccX (Address of modbus object);78 - HCC2 (Address of modbus object);79 - HCC3 (Address of modbus object)
|  | IR | 114 | roomX_associated_to_drying | val_u1 |  | 1 | 650 | 653 |  |  | room.hum_ctrl.drying_supplier_oid | 24 | 100 | roomX | 0 – NONE;650 - AHU 1 (Address of modbus object);651 - AHU 2 (Address of modbus object);652 - AHU 3 (Address of modbus object);653 - AHU 4 (Address of modbus object)
|  | IR | 116 | roomX_associated_to_thermal_integration | val_u1 |  | 1 | 650 | 653 |  |  | room.ti_ctrl.integration_supplier_oid | 24 | 100 | roomX | 0 – NONE;650 - AHU 1 (Address of modbus object);651 _ AHU 2 (Address of modbus object);652 - AHU 3 (Address of modbus object);653 - AHU 4 (Address of modbus object)
|  | IR | 117 | roomX_radiators_state | val_u1 |  | 1 | 0 | 5 |  |  | room.tmp_ctrl.radiator_state | 24 | 100 | roomX | 0 - NONE (not used in this room or load was not detected on at least one output);1 - IDLE;2 – HEATING ;3 – COOLING;4 - BLOCKED_HEATING;5 - BLOCKED_COOLING
|  | IR | 118 | roomX_underfloor_hc_state | val_u1 |  | 1 | 0 | 5 |  |  | room.tmp_ctrl.floor_state | 24 | 100 | roomX | 0 - NONE (not used in this room or load was not detected on at least one output);1 – IDLE;2 - HEATING;3 - COOLING;4 - BLOCKED_HEATING;5 - BLOCKED_COOLING
|  | IR | 119 | roomX_drying_state | val_u1 |  | 1 |  | 3 |  |  | room.hum_ctrl.drying_state | 24 | 100 | roomX | 0 - NONE (not used in this room);1 - IDLE;2 - DRYING;3 – BLOCKED_DRYING
|  | IR | 120 | roomX_thermal_integration_state | val_u1 |  | 1 | 0 | 5 |  |  | room.ti_ctrl.integration_state | 24 | 100 | roomX | 0 - NONE (not used in this room);1 - DLE;2 - HEATING;3 - COOLING;4 – BLOCKED_HEATING;5 - BLOCKED_COOLING
|  | IR | 121 | roomX_ventilation_state | val_u1 |  | 1 | 0 | 3 |  |  |  | 24 | 100 | roomX | 0 - NONE (not used in this room);1 - IDLE;2 – VENTILATING;3 – BLOCKED_VENTILATING
|  | IR | 122 | roomX_blocking_source_radiators | val_u1 |  | 1 |  |  |  |  | room.tmp_ctrl.radiator_blocking | 24 | 100 | roomX | Same as Heating/Cooling blocking source
|  | IR | 123 | roomX_blocking_source_underfloor_hc | val_u1 |  | 1 |  |  |  |  | room.tmp_ctrl.floor_blocking | 24 | 100 | roomX | Same as Heating/Cooling blocking source
|  | IR | 124 | roomX_blocking_source_drying | val_u1 |  | 1 |  |  |  |  | room.hum_ctrl.drying_blocking | 24 | 100 | roomX | Same as Heating/Cooling blocking source
|  | IR | 125 | roomX_blocking_source_integration | val_u1 |  | 1 |  |  |  |  | room.ti_ctrl.integration_blocking | 24 | 100 | roomX | Same as Heating/Cooling blocking source
|  | HR | 101 | roomX_room_name | val_utf8 |  | 1 |  |  |  |  | room.name | 24 | 100 | roomX | String description (32 Bytes, UTF8, NULL terminated)
|  | HR | 117 | roomX_room_mode | val_u1 |  | 1 | 0 | 1 |  |  | room.mode | 24 | 100 | roomX | 0 - SCHEDULE;1 – MANUAL; In SCHEDULE mode, the “Room temperature setpoint” is not used and the room temperature is controlled by scheduler.
|  | HR | 118 | roomX_room_mode_override | val_u1 |  | 1 | 0 | 3 |  |  | room.mode_override | 24 | 100 | roomX | 0 NONE;1 – TEMPORARY;2 - VACATION_AWAY;3 - ADJUST;In override mode (> NONE), the “Room temperaturesetpoint” is not used. The requested temperature is corrected by user via room thermostat or mobile application. You can disable the override mode by setting this value to 0 (NONE)
|  | HR | 119 | roomX_room_temp_setpoint | val_d2_fp100 |  | 1 |  |  |  |  | room.tmp_ctrl.heat.temp_set_manual;room.tmp_ctrl.cool.temp_set_manual | 24 | 100 | roomX | Temperature requested by user.;This values is not used when ;Room mode - SCHEDULE (Scheduler temperature is used);Location.Vacation - ON (Vacation temperature isused);Location.Standby – ON (Standby temperature is used); Temporary mode - activated (User defined temperature is used)
|  | HR | 120 | roomX_user_interface_access_level | val_u1 |  | 1 | 8 | 32 |  |  | room.therm_access_level | 24 | 100 | roomX | 8 – LOCKED (Read Only);16 - HOTEL;32 - UNLOCKED
|  | HR | 121 | roomX_standby_temp | val_d2_fp100 |  | 1 |  |  |  |  | room.tmp_ctrl.heat.temp_set_standby;room.tmp_ctrl.cool.temp_set_standby | 24 | 100 | roomX | Room temperature setpoint used when the system is in Standby mode
|  | HR | 122 | roomX_vacation_temp | val_d2_fp100 |  | 1 |  |  |  |  | room.tmp_ctrl.heat.temp_set_vacation;room.tmp_ctrl.cool.temp_set_vacation | 24 | 100 | roomX | Room temperature setpoint used when the system is in Vacation mode
|  | HR | 123 | roomX_exclude_from_vacation | val_u1 |  | 1 | 0 | 1 |  |  | room.allow_vacation_away | 24 | 100 | roomX | Do not allow the Vacation mode in this room
|  | HR | 124 | roomX_adaptive_mode | val_u1 |  | 1 | 0 | 1 |  |  | room.tmp_ctrl.adaptive_mode_ena | 24 | 100 | roomX | Allow adaptive mode
|  | HR | 125 | roomX_thermal_integration_heating_offset | val_d2_fp100 |  | 1 | 0 | 1000 |  |  | room.ti_ctrl.offset | 24 | 100 | roomX | Thermal integration heating offset
|  | HR | 126 | roomX_thermal_integration_hysteresis | val_d2_fp100 |  | 1 | 10 | 400 |  |  | room.ti_ctrl.hysteresis | 24 | 100 | roomX | Thermal integration hysteresis
|  | HR | 127 | roomX_humidity_threshold_heating | val_d2_fp100 |  | 1 | 2000 | 9000 |  |  | room.hum_ctrl.heat.hum_set_manual | 24 | 100 | roomX | Humidity threshold heating
|  | HR | 128 | roomX_humidity_threshold_cooling | val_d2_fp100 |  | 1 | 2000 | 9000 |  |  | room.hum_ctrl.cool.hum_set_manual | 24 | 100 | roomX | Humidity threshold cooling
|  | HR | 129 | roomX_humidity_hysteresis | val_d2_fp100 |  | 1 | 200 | 500 |  |  | room.hum_ctrl.hum_hysteresis | 24 | 100 | roomX | Humidity hysteresis
|  | HR | 130 | roomX_drying_cooling_water_offset | val_d2_fp100 |  | 1 | -500 | 500 |  |  | room.hum_ctrl.cool.drying_offset | 24 | 100 | roomX | Drying - cooling water offset
|  | HR | 131 | roomX_drying_cooling_water_offset_hysteresis | val_d2_fp100 |  | 1 | 10 | 40 |  |  | room.hum_ctrl.drying_offset_hysteresis | 24 | 100 | roomX | Drying - cooling water offset hysteresis
|  | HR | 132 | roomX_dew_point_cooling_threshold | val_d2_fp100 |  | 1 | 0 | 3000 |  |  | room.hum_ctrl.drying_on_cooling_dew_point_threshold | 24 | 100 | roomX | Dew point threshold temp when cooling
|  | HR | 133 | roomX_dew_point_cooling_threshold_hysteresis | val_d2_fp100 |  | 1 | 10 | 400 |  |  | room.hum_ctrl.drying_on_cooling_dew_point_hysteresis | 24 | 100 | roomX | Dew point threshold temp hysteresis when cooling
|  | HR | 134 | roomX_humidity_high_alarm_limit | val_d2_fp100 |  | 1 | 0 | 10000 |  |  | room.hum_ctrl.hum_alarm_high | 24 | 100 | roomX | Humidity high alarm limit
Outdoor |  | IDR | 3301 | outdoor1_aggregated_warning | bool |  | 1 | [8 empty] | A problem is pending in Outdoor zone
|  | IDR | 3302 | outdoor1_aggregated_error | bool |  | 1 | [8 empty] | A critical problem is pending in Outdoor zone
|  | IDR | 3303 | outdoor1_low_battery_warning | bool |  | 1 |  |  |  |  | device.warn_periph_low_batery |  |  |  | There are one or more peripherals in the Outdoor zone with low battery.
|  | IDR | 3304 | outdoor1_peripheral_lost_error | bool |  | 1 |  |  |  |  | device.warn_periph_unreachable |  |  |  | There are one or more peripherals in the Outdoor zone which are not responding.
|  | IR | 3301 | outdoor1_air_temp | val_d2_fp100 |  | 1 |  |  |  |  | outdoor.outdoor_temp |  |  |  | Used in H/C mode switching, H/C blocking
|  | IR | 3302 | outdoor1_air_temp_filtered | val_d2_fp100 |  | 1 |  |  |  |  | outdoor.filtered_outdoor_temp |  |  |  | Used in heat curve calculations, frost protection
|  | IR | 3303 | outdoor1_air_temp_geometrical | val_d2_fp100 |  | 1 |  |  |  |  | outdoor.average_outdoor_temp |  |  |  | Not yet used
|  | HR | 3301 | outdoor1_name_ | val_utf8 |  | 1 |  |  |  |  | Read only, fixed name "outdoor" |  |  |  | String description (32 Bytes, UTF8, NULL terminated)
|  | HR | 33017 | outdoor1_air_temp_bms_override | val_d2_fp100 |  | 1 |  |  |  |  | outdoor.outdoor_temp_bms_override |  |  |  | Overrides Air Temp value (register 03301)
DHW201 |  | IDR | 6501 | dhw201_aggregated_warning | bool |  | 1 |  |  | - | [5 empty] | A problem is pending in DHW
|  | IDR | 6502 | dhw201_aggregated_error | bool |  | 1 |  |  | - | [5 empty] | A critical problem is pending in DHW
|  | IDR | 6503 | dhw201_retentive_low_energy_warning | bool |  | 1 |  |  |  |  | dhw.calefa_ctrl.warn_low_energy
|  | IDR | 6504 | dhw201_temp_high_error | bool |  | 1 |  |  |  |  | dhw.calefa_ctrl.alarm_high_temp
|  | IDR | 6505 | dhw201_motor_failure_errror | bool |  | 1 |  |  |  |  | dhw.calefa_ctrl. alarm_motor_fail
|  | IDR | 6506 | dhw201_dhi_sensor_failure_error | bool |  | 1 |  |  |  |  | dhw.calefa_ctrl. alarm_dhi_sensor_fail
|  | IDR | 6507 | dhw201_dho_sensor_failure_source_return_error | bool |  | 1 |  |  |  |  | dhw.calefa_ctrl. alarm_dho_sensor_fail
|  | IDR | 6508 | dhw201_sensor_failure_error | bool |  | 1 |  |  |  |  | dhw.calefa_ctrl. alarm_dhw_sensor_fail
|  | IDR | 6509 | dhw201_dcv_sensor_failure_error | bool |  | 1 |  |  |  |  | dhw.calefa_ctrl. alarm_dcw_sensor_fail
|  | IDR | 6510 | dhw201_pressure_high_warning | bool |  | 1 |  |  |  |  | dhw.calefa_ctrl. warn_press_high
|  | IDR | 6511 | dhw201_pressure_low_warning | bool |  | 1 |  |  |  |  | dhw.calefa_ctrl. warn_press_low
|  | IDR | 6512 | dhw201_pressure_critical_low_error | bool |  | 1 |  |  |  |  | dhw.calefa_ctrl. alarm_press_crit_low
|  | IR | 6501 | dhw201_desired_temp | val_d2_fp100 |  | 1 |  |  |  |  | dhw. calefa_ctrl.temp_set |  |  |  | Shows the desired temperature of the domestic hot water.
|  | IR | 6502 | dhw201_state | val_u1 |  | 1 | 1 | 5 | [6 empty] | 1 IDLE ;2 - HEATING (hot water is consumed by user);3 - BYPASS (keeping heat exchanger hot for circulation);4 – BLOCKED_HEATING;5 - BLOCKED_BYPASS; info - (Shows, whether the system wants to heat or to have bypass activated.)
|  | IR | 6503 | dhw201_blocking_source | val_u1 |  | 1 |  |  |  |  | dhw.blocking |  |  |  | Same as Heating/Cooling blocking source
|  | IR | 6504 | dhw201_circulation_state | val_u1 |  | 1 | 0 | 2 |  |  | dhw.circ_ctrl.circ_state;dhw.circ_ctrl.circ_pump_present |  |  |  | 0 - NONE (disabled) ;1 -IDLE ;2 - ON
|  | IR | 6505 | dhw201_measured_temp | val_d2_fp100 |  | 1 | 0 |  |  |  | dhw.calefa_ctrl.dhw_temp |  |  |  | Current temperature of the domestic hot water flowing from DHW
|  | IR | 6506 | dhw201_source_inlet_temp | val_d2_fp100 |  | 1 |  |  |  |  | dhw.calefa_ctrl.hcw_source_inlet_temp |  |  |  | Current temperature of the water incoming from the heat source.
|  | IR | 6507 | dhw201_source_return_temp | val_d2_fp100 |  | 1 |  |  |  |  | dhw.calefa_ctrl.hcw_source_return_temp |  |  |  | Current temperature of the water returning to the heat source.
|  | IR | 6508 | dhw201_pressure | val_d2_fp100 |  | 1 |  |  |  |  | dhw.calefa_ctrl.hcw_pressure |  |  |  | Current pressure of the secondary system
|  | IR | 6509 | dhw201_domestic_cold_water_temp | val_d2_fp100 |  | 1 |  |  |  |  | dhw.calefa_ctrl.dcw_temp |  |  |  | On heat exchanger input
|  | IR | 6510 | dhw201_domestic_cold_water_flow | val_d2 |  | 1 |  |  |  |  | dhw.calefa_ctrl.dcw_flow |  |  |  | Flow meter (analog) in l/h
|  | HR | 6501 | dhw201_name | val_utf8 |  | 1 |  |  |  |  | dhw.name |  |  |  | String description (32 Bytes, UTF8, NULL terminated)
|  | HR | 6517 | dhw201_mode | val_u1 |  | 1 | 0 | 3 |  |  | dhw.mode |  |  |  | 0 - SCHEDULE _x000D_;1 - SCHEDULE_ADAPTIVE _x000D_;2 - ECO _x000D_3 - COMFORT _x000D_ _x000D_ Eco = circulation and hot bypass are disabled _x000D_ Comfort = circulation and hot bypass are enabled
|  | HR | 6518 | dhw201_user_interface_access_level | val_u1 |  | 1 |  | 40 |  |  | dhw.access_level |  |  |  | < 40 USER (user menu) _x000D_ >= 40 INSTALLER (inst. menu)
|  | HR | 6519 | dhw201_block_request | val_u1 |  | 1 | 0 | 1 |  |  | dhw. calefa_ctrl.block_by_bms |  |  |  | 0 - NONE _x000D_;1 - BLOCK_REQUEST _x000D_x000D_ When BLOCK_REQUEST is set, then the system blocks heating and bypass to eliminate consumption from heat supplier.
|  | HR | 6520 | dhw201_power_consumption_limit | val_u2 |  | 1 | 0 | 1 |  |  | dhw. calefa_ctrl.pwr_consumption_limit
|  | HR | 6521 | dhw201_temp_set | val_d2_fp100 |  | 1 |  |  |  |  | dhw. calefa_ctrl.temp_set |  |  |  | Requested temperature of domestic hot water.
|  | HR | 6522 | dhw201_bypass_temp | val_d2_fp100 |  | 1 |  |  |  |  | dhw. calefa_ctrl.bypass_temp_set
|  | HR | 6523 | dhw201_circulation_pump_present | val_u1 |  | 1 | 0 | 1 |  |  | dhw.circ_ctrl.circ_pump_present |  |  |  | 0 – DISABLED;1 - ENABLED (scheduler)
|  | HR | 6524 | dhw201_circulation_inlet_temp | val_d2_fp100 |  | 1 |  |  |  |  | dhw.circ_ctrl. circ_temp_set |  |  |  | When circulation is enabled and there is NO dhw consumption, then the DHW temperature is regulated to this value.
|  | HR | 6525 | dhw201_exclude_from_vacation | val_u1 |  | 1 | 0 | 1 |  |  | dhw.allow_vacation_away |  |  |  | Do not allow the Vacation mode
|  | HR | 6526 | dhw201_exclude_from_standby | val_u1 |  | 1 | 0 | 1 |  |  | dhw.allow_standby |  |  |  | Do not allow the Standby mode
DHWCCU |  | IDR | 6601 | dhwccu_aggregated_warning | bool |  | 1 | [8 empty] | A problem is pending in DHW
|  | IDR | 6602 | dhwccu_aggregated_error | bool |  | 1 | [8 empty] | A critical problem is pending in DHW
|  | IDR | 6603 | dhwccu_cleaning_process_fail_warning | bool |  | 1 |  |  |  |  | dhw.tank_ctrl.warn_cleaning_fail
|  | IDR | 6604 | dhwccu_tank_temp_sensor_fail_error | bool |  | 1 |  |  |  |  | dhw.tank_ctrl.err_tank_sensor_fail
|  | IDR | 6605 | dhwccu_circulation_return_temp_sensor_fail_error | bool |  | 1 |  |  |  |  | dhw.tank_ctrl.err_circ_sensor_fail
|  | IDR | 6606 | dhwccu_source_return_temp_sensor_fail_error | bool |  | 1 |  |  |  |  | dhw.tank_ctrl.err_hcw_return_sensor_fail
|  | IDR | 6607 | dhwccu_source_inlet_temp_sensor_fail_error | bool |  | 1 |  |  |  |  | dhw.tank_ctrl.err_hcw_inlet_sensor_fail
|  | IDR | 6608 | dhwccu_source_inlet_temp_too_low_warning | bool |  | 1 |  |  |  |  | dhw.tank_ctrl.warn_low_hcw_source_temp
|  | IDR | 6609 | dhwccu_peripheral_low_battery_warning | bool |  | 1 |  |  |  |  | dhw.tank_ctrl.warn_periph_low_battery
|  | IDR | 6610 | dhwccu_peripheral_unreachable_error | bool |  | 1 |  |  |  |  | dhw.tank_ctrl.err_periph_unreachable
|  | IR | 6601 | dhwccu_tank_measured_temp | val_d2_fp100 |  | 1 |  |  |  |  | dhw.tank_ctrl.tank_temp |  |  |  | Current temperature of the domestic hot water in the tank
|  | IR | 6602 | dhwccu_tank_desired_temp | val_d2_fp100 |  | 1 |  |  |  |  | dhw.tank_ctrl.temp_desired |  |  |  | Desired temperature of the domestic hot water inside the tank (according to sheduler or manual setup).;NOTE: The tank temperature is different form the temperature flowing from the tip.
|  | IR | 6603 | dhwccu_tank_state | val_u1 |  | 1 | 1 | 5 |  |  | dhw.state;dhw.blocking |  |  |  | 1 - DLE;2 - HEATING;3 - CLEANING;4 – BLOCKED_HEATING;5 - BLOCKED_CLEANING
|  | IR | 6604 | dhwccu_tank_blocking_source | val_u1 |  | 1 |  |  |  |  | dhw.blocking |  |  |  | Same as Heating/Cooling blocking source
|  | IR | 6605 | dhwccu_circulation_state | val_u1 |  | 1 | 0 | 2 |  |  | dhw.circ_ctrl.circ_state;dhw.circ_ctrl.circ_pump_present |  |  |  | 0 - NONE (disabled);1 – IDLE;2 - ON
|  | IR | 6606 | dhwccu_circulation_return_temp | val_d2_fp100 |  | 1 |  |  |  |  | dhw.circ_ctrl.circ_return_temp |  |  |  | Current temperature of the domestic hot water returning from circulation.
|  | IR | 6607 | dhwccu_source_inlet_temp | val_d2_fp100 |  | 1 |  |  |  |  | dhw.tank_ctrl.hcw_source_inlet_temp |  |  |  | Current temperature of the water incoming from the heat source.
|  | IR | 6608 | dhwccu_source_return_temp | val_d2_fp100 |  | 1 |  |  |  |  | dhw.tank_ctrl.hcw_source_return_temp |  |  |  | Current temperature of the water returning to the heat source.
|  | HR | 6601 | dhwccu_name | val_utf8 |  | 1 |  |  |  |  | dhw.name |  |  |  | String description (32 Bytes, UTF8, NULL terminated)
|  | HR | 6617 | dhwccu_mode | val_u1 |  | 1 | 0 | 2 |  |  | dhw.circ_ctrl.circ_pump_present |  |  |  | 0 – SCHEDULE ;2 - ECO = Circulation is disabled
|  | HR | 6618 | dhwccu_circulation_cooldown_time | val_u2 |  | 1 | 300 | 3600 |  |  | dhw.circ_ctrl.circ_cooldown_time |  |  |  | How long the circulation is supressed after is paused due to "Stop temp difference"
|  | HR | 6619 | dhwccu_circulation_temp_difference | val_d2_fp100 |  | 1 | 300 | 2500 |  |  | dhw.circ_ctrl.circ_temp_difference |  |  |  | When difference between tank temperature and return temperature from circulation is lower than this value, the circulation pump is switched off.
|  | HR | 6620 | dhwccu_source_return_temp_limit | val_d2_fp100 |  | 1 | 3000 | 6000 |  |  | dhw.tank_ctrl.hcw_source_return_temp_limit |  |  |  | The controller limits the source return temperature according to this value.;(used only in "advanced tank mode")
|  | HR | 6621 | dhwccu_tank_temp_set | val_d2_fp100 |  | 1 |  |  |  |  | dhw. tank_ctrl.temp_set |  |  |  | Requested temperature of domestic hot water.
|  | HR | 6622 | dhwccu_tank_temp_set_vacation | val_d2_fp100 |  | 1 |  |  |  |  | dhw.tank_ctrl.temp_set_vacation |  |  |  | Requested temperature of domestic hot water in Vacation mode
|  | HR | 6623 | dhwccu_tank_temp_set_cleaning | val_d2_fp100 |  | 1 | 6500 |  |  |  | dhw.tank_ctrl.temp_set_cleaning |  |  |  | Requested temperature of domestic hot water during the cleaning process.
|  | HR | 6624 | dhwccu_tank_temp_set_standby | val_d2_fp100 |  | 1 |  |  |  |  | dhw.tank_ctrl.temp_set_standby |  |  |  | Requested temperature of domestic hot water in Standby mode
|  | HR | 6625 | dhwccu_exclude_from_vacation | val_u1 |  | 1 | 0 | 1 |  |  | dhw.allow_vacation_away |  |  |  | Do not allow the Vacation mode
|  | HR | 6626 | dhwccu_exclude_from_standby | val_u1 |  | 1 | 0 | 1 |  |  | dhw.allow_standby |  |  |  | Do not allow the Standby mode
|  | IDR | 7301 | itcX_aggregated_warning | bool |  | 1 | [5 empty] | 4 | 100 | itcX | A problem is pending in ITC
|  | IDR | 7302 | itcX_aggregated_error | bool |  | 1 | [5 empty] | 4 | 100 | itcX | A critical problem is pending in ITC
|  | IDR | 7303 | itcX_inlet_sensor_failure_error | bool |  | 1 |  |  |  |  | itc.err_inlet_sensor_fail | 4 | 100 | itcX | Missing or broken sensor
|  | IDR | 7304 | itcX_servo_failure_error | bool |  | 1 |  |  |  |  | itc.err_servo_fail | 4 | 100 | itcX | Missing or broken servo
|  | IDR | 7305 | itcX_return_sensor_failure_error | bool |  | 1 |  |  |  |  | itc.err_return_sensor_fail | 4 | 100 | itcX | Missing or broken sensor
|  | IDR | 7306 | itcX_outdoor_sensor_failure_error | bool |  | 1 |  |  |  |  | itc.err_outdoor_sensor_fail | 4 | 100 | itcX | Missing or broken sensor
|  | IDR | 7307 | itcX_high_temp_cut_off_activated_error | bool |  | 1 |  |  |  |  | itc.heat_ctrl.err_htco | 4 | 100 | itcX | Safety mechanism "high temp cut-off" is activated
|  | IDR | 7308 | itcX_frost_protection_activated_error | bool |  | 1 |  |  |  |  | itc.err_frost_protection_active | 4 | 100 | itcX | Safety mechanism "frost protection" is activated
|  | IR | 7301 | itcX_state | val_u1 |  | 1 | 1 | 5 |  |  | itc.state;itc.hcw_blocking | 4 | 100 | itcX | 1 - IDLE_x005F_x000D;_;2 - HEATING_x000D_;3 - COOLING_x000D_;4 – BLOCKED_HEATING_x000D_;5 - BLOCKED_COOLING
|  | IR | 7302 | itcX_blocking_source | val_u1 |  | 1 |  |  |  |  | itc.hcw_blocking | 4 | 100 | itcX | Same as Heating/Cooling blocking source
|  | IR | 7303 | itcX_pump_demand | val_u1 |  | 1 | 1 | 2 |  |  | itc.pump_demand | 4 | 100 | itcX | 1 – IDLE;2 - ON
|  | IR | 7304 | itcX_pump_state | val_u1 |  | 1 | 1 | 2 |  |  | itc.pump_state | 4 | 100 | itcX | 1 – IDLE;2 - ON
|  | IR | 7305 | itcX_measured_inlet_temp | val_d2_fp100 |  | 1 |  |  |  |  | itc.inlet_temp | 4 | 100 | itcX | Measured temperature of the inlet heating/cooling water.
|  | IR | 7306 | itcX_desired_inlet_temp | val_d2_fp100 |  | 1 |  |  |  |  | itc.inlet_temp_desired | 4 | 100 | itcX | Desired temperature of the inlet heating/cooling water. ;The value which the ITC regulator wants to meet.
|  | IR | 7307 | itcX_measured_return_temp | val_d2_fp100 |  | 1 |  |  |  |  | itc.return_temp | 4 | 100 | itcX | Measured return temperature
|  | IR | 7308 | itcX_main_supplier_temp | val_d2_fp100 |  | 1 |  |  |  |  | itc.hcw_supplier_oid.hcw_inlet_temp | 4 | 100 | itcX | Main supplier temperature
|  | HR | 7301 | itcX_name | val_utf8 |  | 1 |  |  |  |  | itc.name | 4 | 100 | itcX | String description (32 Bytes, UTF8, NULL terminated)
|  | HR | 7317 | itcX_regulator_p_value | val_d2_fp10 |  | 1 | 1 | 250 |  |  | itc.heat_ctrl.itc_p_gain | 4 | 100 | itcX | Proportional gain of temperature regulator
|  | HR | 7318 | itcX_regulator_i_value | val_u2 |  | 1 | 5 | 60 |  |  | itc.heat_ctrl.itc_i_time | 4 | 100 | itcX | Integrating time of temperature regulator
|  | HR | 7319 | itcX_regulator_hysteresis | val_d2_fp100 |  | 1 | 10 | 500 |  |  | itc.heat_ctrl.itc_hysteresis | 4 | 100 | itcX | Hysteresis
|  | HR | 7320 | itcX_heat_curve_type | val_u1 |  | 1 | 0 | 3 |  |  | itc.heat_ctrl.curve_type | 4 | 100 | itcX | 0 – MANUAL;1 – CALCULATED;2 – UNDERFLOOR;3 – RADIATORS
|  | HR | 7321 | itcX_heat_curve_manual_slope | val_d2_fp10 |  | 1 | 1 | 40 |  |  | itc.heat_ctrl.curve_manual | 4 | 100 | itcX | Curve slope.;Used only in MANUAL
|  | HR | 7322 | itcX_heat_curve_parallel_displacement | val_d2_fp100 |  | 1 | -900 | 900 |  |  | itc.heat_ctrl.curve_parallel_displacement | 4 | 100 | itcX | Shifts calculated temperature up/down
|  | HR | 7323 | itcX_heat_curve_min_inlet | val_d2_fp100 |  | 1 | 2000 |  |  |  | itc.heat_ctrl.curve_inlet_temp_min | 4 | 100 | itcX | Lowest possible temperature
|  | HR | 7324 | itcX_heat_curve_max_inlet | val_d2_fp100 |  | 1 |  | 8500 |  |  | itc.heat_ctrl.curve_inlet_temp_max | 4 | 100 | itcX | Highest possible temperature
|  | HR | 7325 | itcX_heat_curve_gain | val_d2_fp10 |  | 1 | -20 | 20 |  |  | itc.heat_ctrl.curve_no_ts_gain | 4 | 100 | itcX | Static gain of desired temperature calculation
|  | HR | 7326 | itcX_return_temp_limiter_function | val_u1 |  | 1 | 0 | 2 |  |  | itc.heat_ctrl.return_limiter_mode | 4 | 100 | itcX | 0 - OFF;1 – MIN;2 - MAX
|  | HR | 7327 | itcX_return_temp_max_limiter_limit | val_d2_fp100 |  | 1 | 1000 | 9500 |  |  | itc.heat_ctrl.return_max_limit | 4 | 100 | itcX | Maximum allowed return temperature (limits inlet temperature)
|  | HR | 7328 | itcX_return_temp_max_limiter_gain | val_d2_fp10 |  | 1 | -99 | -1 |  |  | itc.heat_ctrl.return_max_limit_gain | 4 | 100 | itcX | Return limiter proportional gain.;Use high value fast acting system, low value for slow acting system.
|  | HR | 7329 | itcX_return_temp_max_limiter_priority_over_inlet | val_u1 |  | 1 | 0 | 1 |  |  | itc.heat_ctrl.return_max_limit_priority | 4 | 100 | itcX | 0 -NO_PRIORITY;1 -PRIORITY (return limiter can override "Heat curve - min inlet")
|  | HR | 7330 | itcX_return_temp_min_limiter_limit | val_d2_fp100 |  | 1 | 1000 | 9500 |  |  | itc.heat_ctrl.return_min_limit | 4 | 100 | itcX | Minimal allowed return temperature (limits inlet temperature)
|  | HR | 7331 | itcX_return_temp_min_limiter_gain | val_d2_fp10 |  | 1 | 10 | 99 |  |  | itc.heat_ctrl.return_min_limit_gain | 4 | 100 | itcX | Return limiter proportional gain.;Use high value fast acting system, low value for slow acting system.
|  | HR | 7332 | itcX_optimization_boost | val_u1 |  | 1 | 0 | 1 |  |  | itc.heat_ctrl.boost_mode | 4 | 100 | itcX | Boost desired temperature by "Optimization - boost percent" for 1 hour;0 – DISABLED; 1 - ENABLED
|  | HR | 7333 | itcX_optimization_boost_percent | val_u1 |  | 1 | 1 | 100 |  |  | itc.heat_ctrl.boost_level | 4 | 100 | itcX | Boost percent
|  | HR | 7334 | itcX_optimization_ramping | val_u1 |  | 1 | 0 | 1 |  |  | itc.heat_ctrl.ramping_mode | 4 | 100 | itcX | Rise desired temperature over ramping time.;0 – DISABLED; 1 - ENABLED
|  | HR | 7335 | itcX_optimization_ramping_time | val_u1 |  | 1 | 1 | 120 |  |  | itc.heat_ctrl.ramping_time | 4 | 100 | itcX | Ramping time
|  | HR | 7336 | itcX_frost_protection_mode | val_u1 |  | 1 |  |  |  |  | itc.heat_ctrl.frost_protect_mode | 4 | 100 | itcX | Activate heating in assigned loops whe inlet temperature drops bellow "Frost protection - Temp"
|  | HR | 7337 | itcX_frost_protection_temp | val_d2_fp100 |  | 1 | 0 | 1000 |  |  | itc.heat_ctrl.frost_protect_temp | 4 | 100 | itcX | Frost protection limit
|  | HR | 7338 | itcX_high_temp_cut_off_mode | val_u1 |  | 1 | 0 | 1 |  |  | itc.heat_ctrl.htco_mode | 4 | 100 | itcX | Heating is blocked, when inlet temperature exceeds the limit. Alarm is raised, pump is switched off (ignoring all pump delay). 0 DISABLED 1 ENABLED
|  | HR | 7339 | itcX_high_temp_cut-off_temp | val_d2_fp100 |  | 1 | 300 | 2000 |  |  | itc.heat_ctrl.htco_temp | 4 | 100 | itcX | Limit temperature for High Temp Cut-Off
|  | HR | 7340 | itcX_cooling_regulator_p_value | val_d2_fp10 |  | 1 | 1 | 50 |  |  | itc.cool_ctrl.cool_p_gain | 4 | 100 | itcX | Proportional gain of temperature regulator in cooling mode
|  | HR | 7341 | itcX_cooling_regulator_i_value | val_u2 |  | 1 | 5 | 60 |  |  | itc.cool_ctrl.cool_i_time | 4 | 100 | itcX | Integrating time of temperature regulator in cooling mode
|  | HR | 7342 | itcX_cooling_regulator_hysteresis | val_d2_fp100 |  | 1 | 10 | 500 |  |  | itc.cool_ctrl.cool_hysteresis | 4 | 100 | itcX | Hysteresis in cooling mode
|  | HR | 7343 | itcX_cooling_inlet_temp_min | val_d2_fp100 |  | 1 | 1000 |  |  |  | itc.cool_ctrl.cool_inlet_temp_min | 4 | 100 | itcX | Lowest possible temperature in cooling mode
|  | HR | 7344 | itcX_cooling_inlet_temp_max | val_d2_fp100 |  | 1 |  | 3000 |  |  | itc.cool_ctrl.cool_inlet_temp_max | 4 | 100 | itcX | Highest possible temperature in cooling mode
|  | IDR | 7701 | hccX_aggregated_warning | bool |  | 1 | [5 empty] | 4 | 100 | hccX | A problem is pending in ITC
|  | IDR | 7702 | hccX_aggregated_error | bool |  | 1 | [5 empty] | 4 | 100 | hccX | A critical problem is pending in ITC
|  | IDR | 7703 | hccX_inlet_sensor_failure_error | bool |  | 1 |  |  |  |  | hcc.err_inlet_sensor_fail | 4 | 100 | hccX
|  | IDR | 7704 | hccX_high_temp_cut_off_activated_error | bool |  | 1 |  |  |  |  | hcc.heat_ctrl.alarm_htco | 4 | 100 | hccX | Safety mechanism "high temp cut-off" is activated
|  | IR | 7701 | hccX_state | val_u1 |  | 1 | 1 | 5 |  |  | hcc.state;hcc.hcw_blocking | 4 | 100 | hccX | 1 IDLE;2 - HEATING;3 - COOLING;4 – BLOCKED_HEATING;5 - BLOCKED_COOLING
|  | IR | 7702 | hccX_blocking_source | val_u1 |  | 1 |  |  |  |  | hcc.hcw_blocking | 4 | 100 | hccX | Same as Heating/Cooling blocking source
|  | IR | 7703 | hccX_pump_demand | val_u1 |  | 1 | 1 | 2 |  |  | hcc.pump_demand | 4 | 100 | hccX | 1 - IDLE, 2 – ON
|  | IR | 7704 | hccX_pump_state | val_u1 |  | 1 | 1 | 2 |  |  | hcc.pump_state | 4 | 100 | hccX | 1 – IDLE;2 - ON
|  | IR | 7705 | hccX_measured_inlet_temp | val_d2_fp100 |  | 1 |  |  |  |  | hcc.inlet_temp | 4 | 100 | hccX | Measured temperature of the inlet heating/cooling water.
|  | IR | 7706 | hccX_desired_inlet_temp | val_d2_fp100 |  | 1 |  |  |  |  | hcc.hcw_required_temp | 4 | 100 | hccX | Desired temperature of the inlet heating/cooling water. ;The value which the ITC regulator wants to meet.
|  | IR | 7707 | hccX_measured_return_temp | val_d2_fp100 |  | 1 |  |  |  |  | hcc.return_temp | 4 | 100 | hccX | Measured temperature of the return heating/cooling water.
|  | HR | 7701 | hccX_name | val_utf8 |  | 1 |  |  |  |  | hcc.name | 4 | 100 | hccX | String description (32 Bytes, UTF8, NULL terminated)
|  | HR | 7717 | hccX_heat_curve_type | val_u1 |  | 1 | 0 | 3 |  |  | hcc.heat_ctrl.curve_type | 4 | 100 | hccX | 0 - MANUAL;1 - CALCULATED;2 – UNDERFLOOR;3 – RADIATORS
|  | HR | 7718 | hccX_heat_curve_manual_slope | val_d2_fp10 |  | 1 | 1 | 40 |  |  | hcc.heat_ctrl.curve_manual | 4 | 100 | hccX | Curve slope.;Used only in MANUAL
|  | HR | 7719 | hccX_heat_curve_parallel_displacement | val_d2_fp100 |  | 1 | -900 | 900 |  |  | hcc.heat_ctrl.curve_parallel_displacement | 4 | 100 | hccX | Shifts calculated temperature up/down
|  | HR | 7720 | hccX_heat_curve_inlet_temp_min | val_d2_fp100 |  | 1 | 1000 | 8500 |  |  | hcc.heat_ctrl.curve_inlet_temp_min | 4 | 100 | hccX | Lowest possible temperature
|  | HR | 7721 | hccX_heat_curve_inlet_temp_max | val_d2_fp100 |  | 1 | 1000 | 8500 |  |  | hcc.heat_ctrl.curve_inlet_temp_max | 4 | 100 | hccX | Highest possible temperature
|  | HR | 7722 | hccX_heat_curve_gain | val_d2_fp10 |  | 1 | -20 | 20 |  |  | hcc.heat_ctrl.curve_no_ts_gain | 4 | 100 | hccX | Static gain of desired temperature calculation
|  | HR | 7723 | hccX_high_temp_cut_off_mode | val_u1 |  | 1 | 0 | 1 |  |  | hcc.heat_ctrl.htco_mode | 4 | 100 | hccX | Heating is blocked, when inlet temperature exceeds the limit. Alarm is raised, pump is switched off (ignoring all pump delay), 0 DISABLED, 1 ENABLED
|  | HR | 7724 | hccX_high_temp_cut_off_temp | val_d2_fp100 |  | 1 | 1000 | 8500 |  |  | hcc.heat_ctrl.htco_temp;hcc.heat_ctrl.htco_relative_temp | 4 | 100 | hccX | Limit temperature for High Temp Cut-Off
H/C source |  | IDR | 8101 | hc_source1_aggregated_warning | bool |  | 1 | [8 empty] | A problem is pending in H/C Source
|  | IDR | 8102 | hc_source1_aggregated_error | bool |  | 1 | [8 empty] | A critical problem is pending in H/C Source
|  | IDR | 8103 | hc_source1_general_failure_error | bool |  | 1 |  |  |  |  | hcw.err_source_general_failure |  |  |  | General failure
|  | IR | 8101 | hc_source1_state | val_u1 |  | 1 | 1 | 5 |  |  | hcw.hcw_status;hcw.hcw_blocking |  |  |  | 1 – IDLE;2 – HEATING;3 - COOLING;4 – BLOCKED_HEATING;5 - BLOCKED_COOLING
Peripheral |  | IDR | 51201 | peripheralX_aggregated_warning | bool |  | 1 | [5 empty] | 64 | 100 | peripheralX | A problem is pending in Room
|  | IDR | 51202 | peripheralX_aggregated_error | bool |  | 1 | [5 empty] | 64 | 100 | peripheralX | A critical problem is pending in Room
|  | IDR | 51203 | peripheralX_low_battery_warning | bool |  | 1 |  |  |  |  | device.warn_low_batery | 64 | 100 | peripheralX | Battery is low in the peripheral.
|  | IDR | 51204 | peripheralX_peripheral_lost_error | bool |  | 1 |  |  |  |  | device.warn_unreachable | 64 | 100 | peripheralX | Peripheral is not responding.
|  | IR | 51201 | peripheralX_type | val_u2 |  | 1 |  |  |  |  | GetProductType(device.sn) | 64 | 100 | peripheralX | Peripheral type - Sensor, Termostat, see table at the top
|  | IR | 51202 | peripheralX_sn | val_u4 |  | 1 |  |  |  |  | device.sn | 64 | 100 | peripheralX | Serial number
|  | IR | 51204 | peripheralX_owner | val_u2 |  | 1 | 0 | 16 |  |  | GetModbusAddress(device.owner_id) | 64 | 100 | peripheralX | 000 – Location, 001 - Room 1 ..016 - Room 16 NOTE: Object address in this modbus table is used as owner_id
|  | IR | 51205 | peripheralX_signal_strength | val_u1 |  | 1 |  | 6 |  |  | Min(device.signal_strength_tx, device.signal_strength_rx) | 64 | 100 | peripheralX | Peripheral Signal strength 0 - 6, ;0 - worst signal…6 - best signal
|  | HR | 51201 | peripheralX_name | val_utf8 |  | 1 |  |  |  |  | device.name | 64 | 100 | peripheralX | String description (32 Bytes, UTF8, NULL terminated)
Dehumidifer |  | IDR | 65001 | dehumidifierX_aggregated_warning | bool |  | 1 | [5 empty] | 4 | 100 | dehumidifierX | A problem is pending in device
|  | IDR | 65002 | dehumidifierX_aggregated_error | bool |  | 1 | [5 empty] | 4 | 100 | dehumidifierX | A critical problem is pending in device
|  | IDR | 65003 | dehumidifierX_air_filter_lifetime_expired_warning | bool |  | 1 |  |  |  |  | edevMVDI.warn_air_filter_replace | 4 | 100 | dehumidifierX | Air filter lifetime expired = 1
|  | IDR | 65004 | dehumidifierX_air_filter_solar_year_passed_warning | bool |  | 1 |  |  |  |  | edevMVDI.warn_air_filter_replace | 4 | 100 | dehumidifierX | Air filter solar year passed from last air filter change = 2
|  | IDR | 65005 | dehumidifierX_hcw_supplier_error | bool |  | 1 |  |  |  |  | edevMVDI.err_no_hcw_supplier | 4 | 100 | dehumidifierX | Heating/Cooling water supplier is not set
|  | IDR | 65006 | dehumidifierX_fault_error | bool |  | 1 |  |  |  |  | edevMVDI.err_device_fault | 4 | 100 | dehumidifierX | Device fault - general signal from device
|  | IR | 65001 | dehumidifierX_type | val_u1 |  | 1 | 1 | 2 |  |  | edevMVDI.type | 4 | 100 | dehumidifierX | 0 -GENERIC;1 – P300_S300; 2 - PC300_SC300
|  | IR | 65003 | dehumidifierX_drying_status | val_u1 |  | 1 | 2 | 3 |  |  | edevMVDI.drying_state | 4 | 100 | dehumidifierX | 0 - NONE (function not available);1 - IDLE;2 – DRYING,3 -BLOCKED_DRYING
|  | IR | 65004 | dehumidifierX_drying_blocking | val_u1 |  | 1 |  |  |  |  | edevMVDI.drying_blocking | 4 | 100 | dehumidifierX | Please check top of the document - GENERAL BLOCKING SOURCES
|  | IR | 65005 | dehumidifierX_thermal_status | val_u1 |  | 1 | 0 | 5 |  |  | edevMVDI.integration_state | 4 | 100 | dehumidifierX | 0 - NONE (function not available);1 – IDLE;2 - HEATING;3 – COOLING;4 – BLOCKED_HEATING;5 – BLOCKED_COOLING
|  | IR | 65006 | dehumidifierX_thermal_blocking | val_u1 |  | 1 |  |  |  |  | edevMVDI.integration_blocking | 4 | 100 | dehumidifierX | Please check top of the document - GENERAL BLOCKING SOURCES
|  | IR | 65007 | dehumidifierX_thermal_demand_condition | val_u1 |  | 1 | 100 | 101 |  |  | edevMVDI.integAggregator.demand_condition | 4 | 100 | dehumidifierX | 100 - IN ANY ROOM;101 - IN ALL ROOMS(1-32 PARTICULAR ROOM (Address of modbus object))
|  | IR | 65010 | dehumidifierX_air_filter_last_change | val_u4 |  | 1 |  |  |  |  | edevMVDI.air_filter_last_change | 4 | 100 | dehumidifierX | Timestamp, updates when register "Air filter lifetime used" is set to zero
|  | IR | 65012 | dehumidifierX_associated_hcw_supplier | val_u1 |  | 1 | 0 | 81 |  |  | edevMVDI.hcw_supplier_oid | 4 | 100 | dehumidifierX | 0 – NONE;73 - ITC1 (Address of modbus object);74 - ITC2 (Address of modbus object);77 - hccX (Address of modbus object);78 - HCC2 (Address of modbus object);79 -HCC3 (Address of modbus object);81 – H/C Source (Address of modbus object)
|  | HR | 65001 | dehumidifierX_name | val_utf8 |  | 1 |  |  |  |  | device.name | 4 | 100 | dehumidifierX | String description (32 Bytes, UTF8, NULL terminated)
|  | HR | 65017 | dehumidifierX_air_filter_lifetime | val_u4 |  | 1 | 43200 | 1200000 |  |  | edevMVDI.air_filter_lifetime | 4 | 100 | dehumidifierX | Air filter lifetime (minutes)
|  | HR | 65019 | dehumidifierX_air_filter_lifetime_used | val_u4 |  | 1 |  | 1200000 |  |  | edevMVDI.air_filter_lifetime_used | 4 | 100 | dehumidifierX | Write 0 to reset timer
|  | HR | 65021 | dehumidifierX_drying_mode | val_u1 |  | 1 | 0 | 2 |  |  | edevMVDI.dryingAggregator.allow_mode | 4 | 100 | dehumidifierX | 0 - IN COOLING MODE;1 - IN HEATING MODE;2 - IN BOTH
|  | HR | 65022 | dehumidifierX_drying_desired_cooling_water | val_d2_fp100 |  | 1 | 500 | 3000 |  |  | edevMVDI.drying_required_cooling_water_temp | 4 | 100 | dehumidifierX | Desired cooling water temperature
|  | HR | 65023 | dehumidifierX_mode | val_u1 |  | 1 | 0 | 2 |  |  | edevMVDI.integAggregator.allow_mode | 4 | 100 | dehumidifierX | 0 - IN COOLING MODE;1 - IN HEATING MODE;2 - IN BOTH
|  | HR | 65024 | dehumidifierX_desired_heating_water_temp | val_d2_fp100 |  | 1 | 2000 | 5000 |  |  | edevMVDI.integration_required_heating_water_temp | 4 | 100 | dehumidifierX | Desired heating water temperature
|  | HR | 65025 | dehumidifierX_desired_cooling_water_temp | val_d2_fp100 |  | 1 | 500 | 3000 |  |  | edevMVDI.integration_required_cooling_water_temp | 4 | 100 | dehumidifierX | Desired cooling water temperature
Ventilation |  | IDR | 61001 | ventilationX_aggregated_warning | bool |  | 1 | [5 empty] | 2 | 100 | ventilationX | A problem is pending in device
|  | IDR | 61002 | ventilationX_aggregated_error | bool |  | 1 | [5 empty] | 2 | 100 | ventilationX | A critical problem is pending in device
|  | IDR | 61003 | ventilationX_air_filter_lifetime_expired_warning | bool |  | 1 |  |  |  |  | edevMVDI.warn_air_filter_replace | 2 | 100 | ventilationX | Air filter lifetime expired = 1
|  | IDR | 61004 | ventilationX_air_filter_solar_year_passed_warning | bool |  | 1 |  |  |  |  | edevMVDI.warn_air_filter_replace | 2 | 100 | ventilationX | Air filter solar year passed from last air filter change = 2
|  | IDR | 61005 | ventilationX_device_specific_warning | bool |  | 1 |  |  |  |  | edevMVDI.device_specific_warning | 2 | 100 | ventilationX | Read code from input register - Warning-device specific
|  | IDR | 61006 | ventilationX_device_fault_error | bool |  | 1 |  |  |  |  | edevMVDI.err_device_fault = 1 | 2 | 100 | ventilationX | General problem
|  | IDR | 61007 | ventilationX_communication_error | bool |  | 1 |  |  |  |  | edevMVDI.err_device_fault = 2 | 2 | 100 | ventilationX | Communication problem
|  | IDR | 61008 | ventilationX_not_compatible_error | bool |  | 1 |  |  |  |  | edevMVDI.err_device_fault = 3 | 2 | 100 | ventilationX | Not compatible
|  | IDR | 61009 | ventilationX_device_specific_error | bool |  | 1 |  |  |  |  | edevMVDI.device_specific_error | 2 | 100 | ventilationX | Read code from input register - Error-device specific
|  | IR | 61001 | ventilationX_device_model | val_utf8 |  | 1 |  |  |  |  | edevMVDI.MV.device_model | 2 | 100 | ventilationX | Device model
|  | IR | 61002 | ventilationX_warning_device_specific_code | val_u4 |  | 1 |  |  |  |  | edevMVDI.device_specific_warning | 2 | 100 | ventilationX | Device specific warning code
|  | IR | 61003 | ventilationX_error_device_specific_code | val_u4 |  | 1 |  |  |  |  | edevMVDI.device_specific_error | 2 | 100 | ventilationX | Device specific error code
|  | IR | 61004 | ventilationX_device_feature_bits | val_u4 |  | 1 |  |  |  |  | edevMVDI.MV.device_features | 2 | 100 | ventilationX | Specific features (capabilities) device has 0x0001 - ALLOW_UNOCCUPIED 0x0002 - ALLOW_ECO 0x0004 - ALLOW_COMFORT 0x0008 - ALLOW_STOPPED 0x0010 - ALLOW_BOOST 0x0020 - ALLOW_BYPASS 0x0040 - FAN_PWM_CONTROL 0x0080 - FAN_BINARY_CONTROL 0x0100 - TEMP_INTAKE 0x0200 - TEMP_SUPPLY 0x0400 - TEMP_EXTRACT 0x0800 - TEMP_EXHAUST 0x1000 - HUMIDITY_INTAKE 0x2000 - HUMIDITY_EXTRACT 0x4000 - FAN_SPEED_FEEDBACK
|  | IR | 61005 | ventilationX_ventilation_state | val_u1 |  | 1 | 0 | 11 |  |  | common.ventilation.ventlation_src_status.actual_level, common.ventilation.ventlation_src_status.blocking | 2 | 100 | ventilationX | 0 - STOPPED 1 - UNOCCUPIED 2 - ECONOMY 3 - COMFORT 4 - BOOST 5 - BLOCKED_STOPPED 6 - BLOCKED_UNOCCUPIED 7 - BLOCKED_ECONOMY 8 - BLOCKED_COMFORT 9 - BLOCKED_BOOST 10 - FAILURE 11 - MAINTENANCE
|  | IR | 61006 | ventilationX_ventilation_blocking | val_u1 |  | 1 |  |  |  |  | common.ventilation.ventlation_src_status.blocking | 2 | 100 | ventilationX | Please check top of the document - GENERAL BLOCKING SOURCES
|  | IR | 61007 | ventilationX_supply_fan_speed_actual | val_u2 |  | 1 |  |  |  |  | edevMVDI.MV.fan_speed_supply_rpm | 2 | 100 | ventilationX | Supply fan speed actual (rpm)
|  | IR | 61008 | ventilationX_exhaust_fan_speed_actual | val_u2 |  | 1 |  |  |  |  | edevMVDI.MV.fan_speed_exhaust_rpm | 2 | 100 | ventilationX | Exhaust fan speed actual (rpm)
|  | IR | 61009 | ventilationX_supply_fan_speed_setpoint | val_d2_fp100 |  | 1 |  |  |  |  | edevMVDI.MV.fan_speed_supply | 2 | 100 | ventilationX | Supply fan speed setpoint (%)
|  | IR | 61010 | ventilationX_exhaust_fan_speed_setpoint | val_d2_fp100 |  | 1 |  |  |  |  | edevMVDI.MV.fan_speed_exhaust | 2 | 100 | ventilationX | Exhaust fan speed setpoint (%)
|  | IR | 61011 | ventilationX_supply_volume_flow_setpoint | val_u2 |  | 1 |  |  |  |  | edevMVDI.MV.supply_volume_flow | 2 | 100 | ventilationX | Supply volume flow setpoint (m^3/h)
|  | IR | 61012 | ventilationX_exhaust_volume_flow_setpoint | val_u2 |  | 1 |  |  |  |  | edevMVDI.MV.exhaust_volume_flow | 2 | 100 | ventilationX | Exhaust volume flow setpoint (m^3/h)
|  | IR | 61013 | ventilationX_intake_air_temperature | val_d2_fp100 |  | 1 |  |  |  |  | edevMVDI.MV.temp_intake | 2 | 100 | ventilationX | Intake air temperature
|  | IR | 61014 | ventilationX_supply_air_temperature | val_d2_fp100 |  | 1 |  |  |  |  | edevMVDI.MV.temp_supply | 2 | 100 | ventilationX | Supply air temperature
|  | IR | 61015 | ventilationX_extract_air_temperature | val_d2_fp100 |  | 1 |  |  |  |  | edevMVDI.MV.temp_extract | 2 | 100 | ventilationX | Extract air temperature
|  | IR | 61016 | ventilationX_exhaust_air_temperature | val_d2_fp100 |  | 1 |  |  |  |  | edevMVDI.MV.temp_exhaust | 2 | 100 | ventilationX | Exhaust air temperature
|  | IR | 61017 | ventilationX_heat_recovery_bypass_damper_position | val_d2_fp100 |  | 1 | 0 | 100 |  |  | edevMVDI.MV.bypass_damper_position | 2 | 100 | ventilationX | Heat recovery bypass damper position (%)
|  | IR | 61018 | ventilationX_free_cooling_enabled | val_u1 |  | 1 | 0 | 1 |  |  | edevMVDI.MV.free_cooling_enabled | 2 | 100 | ventilationX | Free cooling enabled
|  | IR | 61019 | ventilationX_air_filter_last_change | val_u4 |  | 1 |  |  |  |  | edevMVDI.air_filter_last_change | 2 | 100 | ventilationX | Timestamp, updates when register "Air filter lifetime used" is set to zero
|  | HR | 61001 | ventilationX_device_name | val_utf8 |  | 1 |  |  |  |  | device.name | 2 | 100 | ventilationX | String description (32 Bytes, UTF8, NULL terminated)
|  | HR | 61017 | ventilationX_air_filter_lifetime | val_u4 |  | 1 | 43200 | 518400 |  |  | edevMVDI.air_filter_lifetime | 2 | 100 | ventilationX | Air filter lifetime (minutes) - maximum value is dependent on device model
|  | HR | 61019 | ventilationX_air_filter_lifetime_used | val_u4 |  | 1 |  |  |  |  | edevMVDI.air_filter_lifetime_used | 2 | 100 | ventilationX | Write 0 to reset timer
|  | HR | 61021 | ventilationX_exhaust_fan_level_unoccupied | val_d2_fp100 |  | 1 |  |  |  |  | edevMVDI.MV.exhaust_fan_level_unoccupied_percent | 2 | 100 | ventilationX | Exhaust Fan Level Unoccupied (%)
|  | HR | 61022 | ventilationX_exhaust_fan_level_eco | val_d2_fp100 |  | 1 |  |  |  |  | edevMVDI.MV.exhaust_fan_level_eco_percent | 2 | 100 | ventilationX | Exhaust Fan Level Eco (%)
|  | HR | 61023 | ventilationX_exhaust_fan_level_comfort | val_d2_fp100 |  | 1 |  |  |  |  | edevMVDI.MV.exhaust_fan_level_comfort_percent | 2 | 100 | ventilationX | Exhaust Fan Level Comfort (%)
|  | HR | 61024 | ventilationX_exhaust_fan_level_boost | val_d2_fp100 |  | 1 |  |  |  |  | edevMVDI.MV.exhaust_fan_level_boost_percent | 2 | 100 | ventilationX | Exhaust Fan Level Boost (%)
|  | HR | 61025 | ventilationX_supply_fan_level_unoccupied | val_d2_fp100 |  | 1 |  |  |  |  | edevMVDI.MV.supply_fan_level_unoccupied_percent | 2 | 100 | ventilationX | Supply Fan Level Unoccupied (%)
|  | HR | 61026 | ventilationX_supply_fan_level_eco | val_d2_fp100 |  | 1 |  |  |  |  | edevMVDI.MV.supply_fan_level_eco_percent | 2 | 100 | ventilationX | Supply Fan Level Eco (%)
|  | HR | 61027 | ventilationX_supply_fan_level_comfort | val_d2_fp100 |  | 1 |  |  |  |  | edevMVDI.MV.supply_fan_level_comfort_percent | 2 | 100 | ventilationX | Supply Fan Level Comfort (%)
|  | HR | 61028 | ventilationX_supply_fan_level_boost | val_d2_fp100 |  | 1 |  |  |  |  | edevMVDI.MV.supply_fan_level_boost_percent | 2 | 100 | ventilationX | Supply Fan Level Boost (%)
|  | HR | 61029 | ventilationX_exhaust_fan_level_unoccupied | val_u2 |  | 1 |  |  |  |  | edevMVDI.MV.exhaust_fan_level_unoccupied_vol | 2 | 100 | ventilationX | Exhaust Fan Level Unoccupied (m^3/h)
|  | HR | 61030 | ventilationX_exhaust_fan_level_eco | val_u2 |  | 1 |  |  |  |  | edevMVDI.MV.exhaust_fan_level_eco_vol | 2 | 100 | ventilationX | Exhaust Fan Level Eco (m^3/h)
|  | HR | 61031 | ventilationX_exhaust_fan_level_comfort | val_u2 |  | 1 |  |  |  |  | edevMVDI.MV.exhaust_fan_level_comfort_vol | 2 | 100 | ventilationX | Exhaust Fan Level Comfort (m^3/h)
|  | HR | 61032 | ventilationX_exhaust_fan_level_boost | val_u2 |  | 1 |  |  |  |  | edevMVDI.MV.exhaust_fan_level_boost_vol | 2 | 100 | ventilationX | Exhaust Fan Level Boost (m^3/h)
|  | HR | 61033 | ventilationX_exhaust_Fan_level_boost | val_u2 |  | 1 |  |  |  |  | edevMVDI.MV.supply_fan_level_unoccupied_vol | 2 | 100 | ventilationX | Supply Fan Level Unoccupied (m^3/h)
|  | HR | 61034 | ventilationX_supply_fan_level_eco | val_u2 |  | 1 |  |  |  |  | edevMVDI.MV.supply_fan_level_eco_vol | 2 | 100 | ventilationX | Supply Fan Level Eco (m^3/h)
|  | HR | 61035 | ventilationX_supply_fan_level_comfort | val_u2 |  | 1 |  |  |  |  | edevMVDI.MV.supply_fan_level_comfort_vol | 2 | 100 | ventilationX | Supply Fan Level Comfort (m^3/h)
|  | HR | 61036 | ventilationX_supply_fan_level_boost | val_u2 |  | 1 |  |  |  |  | edevMVDI.MV.supply_fan_level_boost_vol | 2 | 100 | ventilationX | Supply Fan Level Boost (m^3/h)
|  | HR | 61037 | ventilationX_allow_stopped_level | val_u1 |  | 1 | 0 | 1 |  |  | edevMVDI.MV.allow_stopped_level | 2 | 100 | ventilationX | Allow Stopped level 0 - NOT ALLOWED 1 - ALLOWED
|  | HR | 61038 | ventilationX_allow_unoccupied_level | val_u1 |  | 1 | 0 | 1 |  |  | edevMVDI.MV.allow_unoccupied_level | 2 | 100 | ventilationX | Allow Unoccupied level 0 - NOT ALLOWED 1 - ALLOWED
|  | HR | 61039 | ventilationX_standby_mode_level | val_u1 |  | 1 | 0 | 2 |  |  | edevMVDI.MV.standby_level | 2 | 100 | ventilationX | 0 - STOPPED 1 - UNOCCUPIED 2 - ECONOMY
|  | HR | 61040 | ventilationX_vacation_mode_level | val_u1 |  | 1 | 0 | 2 |  |  | edevMVDI.MV.vacation_level | 2 | 100 | ventilationX | 0 - STOPPED 1 - UNOCCUPIED 2 - ECONOMY
|  | HR | 61041 | ventilationX_heat_exchange_mode | val_u1 |  | 1 | 0 | 1 |  |  | edevMVDI.MV.bypass_mode | 2 | 100 | ventilationX | 0 - ALWAYS ON 1 - AUTOMATIC